Replacement / Upgrade of Ventilation Systems in a Hospital
Aligned to RIBA Plan of Work 2020 & relevant SHTMs

Primary SHTM / Guidance References

| System Element | Key Guidance |
| --- | --- |
| Ventilation Systems | SHTM 03-01 Part A (Design & validation) and Part B (Operational management & performance verification) |
| Overarching | SHTM 00 – Policies and principles |
| Linked Systems | SHTM 06-01 (Electrical services), BMS interfaces, Fire strategy interfaces |
| Core Standards | CDM 2015, relevant BS/EN standards, CIBSE Guides, manufacturer requirements |

Key Principles

- Continuity of ventilation to clinical areas (especially critical care, theatres, isolation rooms) must be maintained.

- HAI-SCRIBE involvement is High across design, construction and handover.

- Ventilation Safety Group (VSG) / Infection Prevention & Control engagement is required.

- Validation and performance verification in accordance with SHTM 03-01 are mandatory.

Key Governance Rule
A clear Pre-Contract Hold Point exists inside Stage 4.
No contractor appointment and no Stage 5 works may proceed until:

- Minimum two competitive quotes have been obtained (with contingency), and

- Formal lifecycle/cost approval has been received from the PFI Board or NHS, and

- Written approval of the SBAR (or equivalent formal submission) has been received from the Ventilation Safety Group / IPC as required.

Stage 0 – Strategic Definition

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Business case / need identification (system condition, clinical risk, air quality, energy performance) |  | SHTM 00, SHTM 03-01 |
| Strategic brief & project outcomes (continuity of ventilation, resilience, clinical safety, efficiency) |  | SHTM 00 |
| High-level clinical / operational impact assessment |  | SHTM 00, SHTM 03-01 |

Stage 1 – Preparation and Briefing

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Project Brief (scope of ventilation replacement, critical areas, continuity requirements) |  | SHTM 00, SHTM 03-01 |
| Existing system condition surveys & baseline data (air volumes, pressures, filtration, hygiene) |  | SHTM 03-01 Part A |
| Initial risk register (service continuity, infection control, access, temporary plant) |  | SHTM 00, CDM, HAI-SCRIBE |
| Project Execution Plan & procurement strategy |  | — |
| Early engagement with Ventilation Safety Group / IPC |  | SHTM 03-01, HAI-SCRIBE |

Stage 2 – Concept Design

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Concept design options (phased replacement, temporary ventilation strategy, AHU type) |  | SHTM 03-01 Part A |
| Outline ventilation strategy (air change rates, pressure regimes, filtration, resilience) |  | SHTM 03-01 Part A |
| Preliminary schematics and load assessment |  | SHTM 03-01 |
| Outline specifications & preliminary cost plan |  | — |
| Design risk assessment (including infection control) |  | CDM, SHTM 00, HAI-SCRIBE |

Stage 3 – Spatial Coordination

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Coordinated design (AHU locations, duct routes, plant access, temporary arrangements) |  | SHTM 03-01 Part A |
| Spatial coordination with structure, electrical, BMS, fire compartments and other services |  | SHTM 00 |
| Updated cost plan, risk register & high-level phasing / temporary ventilation strategy (principles only) |  | — |
| Confirmation of critical area resilience requirements |  | SHTM 03-01 |

Stage 4 – Technical Design

(Contains the Pre-Contract Hold Point)

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Developed design / performance specifications (sufficient for accurate pricing) |  | Not full construction-issue drawings |
| Detailed Scope of Works |  | Clear boundaries |
| Updated cost plan including appropriate contingency |  | Realistic budget envelope |
| Filter & hygiene strategy |  | SHTM 03-01 |
| BMS / controls philosophy and point schedules |  | SHTM 06-01 |
| Electrical design associated with AHUs, fans and controls |  | SHTM 06-01 |
| Duct insulation specification |  | — |
| Building Regulations / statutory compliance information |  | — |
| Designer’s Risk Assessment & residual risks |  | CDM, SHTM 03-01, HAI-SCRIBE |
| Pre-construction information & input to Construction Phase Plan |  | CDM |
| Tender documentation / Scope of Works / pricing schedules |  | — |
| Obtain minimum of two competitive quotations |  | Critical commercial requirement |
| Prepare and submit formal SBAR (or equivalent) to the Ventilation Safety Group / IPC |  | SHTM 03-01, HAI-SCRIBE |
| Obtain written VSG / IPC approval |  | — |
| Submit quotations, cost comparison, contingency and recommendation to PFI Board / NHS for lifecycle approval |  | — |
| PRE-CONTRACT HOLD POINT: No contractor appointment and no further progression until written PFI/NHS cost approval and VSG/IPC approval are both received |  | Clear commercial & governance cut-off |
| After approval and contractor appointment: complete full technical drawings, final coordination and any remaining design details |  | Post-appointment activity still recorded under Stage 4 |

Stage 5 – Manufacturing and Construction

(Only after Stage 4 Hold Point is cleared and contractor is onboarded)

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Contractor’s detailed Method Statements, full RAMS and detailed temporary ventilation arrangements |  | Only after appointment |
| Temporary plant installation, connection, testing & commissioning certificates (if used) |  | SHTM 00 |
| Material & equipment certificates |  | SHTM 03-01 |
| System isolation / shutdown records |  | — |
| Installation of new AHUs, ductwork, fans, filters, controls and associated works |  | SHTM 03-01 Part A |
| Cleanliness & hygiene records during installation |  | SHTM 03-01 |
| BMS installation, wiring, point-to-point testing & sequence proving |  | SHTM 06-01 |
| Electrical installation & test certificates (BS 7671) |  | SHTM 06-01 |
| Progress records, quality inspections & change control log |  | — |
| Decommissioning & strip-out records of redundant plant |  | — |

Stage 6 – Handover

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Full system testing, commissioning and validation records |  | SHTM 03-01 Part A |
| Performance verification data (air volumes, pressures, filtration efficiency, etc.) |  | SHTM 03-01 |
| As-fitted drawings & schematics |  | SHTM 03-01 |
| Comprehensive O&M manuals |  | SHTM 00, SHTM 03-01 Part B |
| Updated Health & Safety File |  | CDM |
| Training & demonstration records for estates / operational staff |  | SHTM 00 |
| Residual risk register |  | CDM |
| Practical Completion / handover certificate |  | — |
| Final validation reports |  | SHTM 03-01 Part A |
| Temporary plant decommissioning & removal certificates (if applicable) |  | — |
| Formal VSG / IPC acceptance |  | SHTM 03-01 Part B |

Stage 7 – Use

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Soft landings / post-occupancy evaluation (performance, resilience, energy, clinical feedback) |  | SHTM 00 |
| Updated Ventilation management arrangements / Written Scheme |  | SHTM 03-01 Part B |
| Ongoing monitoring, verification and maintenance regime |  | SHTM 03-01 Part B |
| Defects liability records & final account |  | — |
| Lessons learned report |  | SHTM 00 |

Cross-Stage / Continuous Deliverables

- Live Health & Safety File

- Project risk register (updated at each stage)

- Change control log

- Ventilation Safety Group / IPC engagement and formal approvals

- HAI-SCRIBE process applied at all relevant stages

- Evidence of compliance with manufacturer instructions and SHTM 03-01

- Maintenance of continuous ventilation to critical clinical areas throughout the works