Project Plan: UPS Battery Backup Upgrade Forth Valley Royal Hospital, NHS Forth Valley Aligned to RIBA Plan of Work 2020 with Clear Stage-Gate Deliverables Version: Full Updated Overview & Plan Date: August 2026

1. Project Overview

| Item | Detail |
| --- | --- |
| Project Title | UPS Systems Replacement – 4 Main Systems (12 units) |
| Location | Forth Valley Royal Hospital, Larbert, Scotland |
| Client | NHS Forth Valley – Estates & Facilities |
| Scope | Full replacement of 12 UPS units (mixed ratings including 80 kVA, 60 kVA and 10 kVA) across 4 independent systems. Works executed in controlled consecutive weekend pairs with a maximum of 2 systems active concurrently. |
| Key Constraints | Live operational hospital; continuous power to critical clinical loads; no unplanned downtime; strict weekend working windows; infection control and fire safety requirements. |
| Strategic Drivers | Ageing existing UPS units, reliability risk to patient safety, compliance with current standards, and improved resilience. |
| Overall Duration | Approximately 10–14 weeks from Stage 2 approval to Stage 6 Practical Completion (subject to procurement lead times). |
| Procurement Route | To be confirmed (direct award or competitive tender). Lead times for UPS units will drive the installation programme. |

The project is managed as a specialist M&E replacement within an operational healthcare environment and follows the RIBA Plan of Work 2020 stage-gate process, adapted for this type of works.

2. RIBA Stage Gate Process – Summary

| RIBA Stage | Stage Name | Core Focus | Primary Gate Approvers |
| --- | --- | --- | --- |
| 0 | Strategic Definition | Need confirmation & high-level viability | Project Sponsor / Estates Director |
| 1 | Preparation and Briefing | Project brief, surveys & baseline data | Estates Lead + Infection Control |
| 2 | Concept Design | Preferred technical solution & phasing | Authorised Person (AP) + Clinical stakeholders |
| 3 | Spatial Coordination | Space, access & interface resolution | Estates + Fire Safety (if required) |
| 4 | Technical Design | Complete compliant design package | AP + Authorising Engineer (AE) + Principal Designer |
| 5 | Manufacturing & Construction | Procurement, installation & progressive testing | AP (progressive after each system pair) |
| 6 | Handover | Commissioning, documentation & Acceptance to Service | AP + AE + Estates Manager |
| 7 | Use | Defects monitoring & lessons learned | Estates |

Stage Gate Rule: No stage may proceed without formal written approval of the required deliverables listed below.

3. Detailed Stage Plans with Mandatory Deliverables

Stage 0 – Strategic Definition

Objective: Confirm strategic need and high-level viability.

Mandatory Deliverables to Pass Gate

- Strategic Brief (clinical risk of existing systems, options appraisal)

- High-level Risk Register (patient safety and power continuity focus)

- Confirmation of affected load categories against SHTM 06-01

- Outline Business Case / funding confirmation

- Initial Stakeholder Map

Stage 1 – Preparation and Briefing

Objective: Establish a robust project brief and baseline information.

Mandatory Deliverables to Pass Gate

- Project Brief (full scope, constraints, success criteria, weekend working rules)

- Complete Load Survey and existing UPS Condition Report

- Preliminary Programme (including concurrent weekend strategy – max 2 systems)

- Initial Health & Safety Strategy and HAI-SCRIBE assessment

- Expanded Risk Register

- Stakeholder Engagement Plan and early consultation records

- Confirmation of any Group 1 or Group 2 medical locations affected (BS 7671 Section 710)

Stage 2 – Concept Design

Objective: Define the preferred technical solution and phasing.

Mandatory Deliverables to Pass Gate

- Concept Design Report (UPS topology, redundancy level, bypass strategy, temporary power arrangements)

- Outline UPS and battery specification

- Preliminary Method Statements and high-level RAMS

- Concept single-line diagrams

- Updated Programme showing concurrent weekend pairs

- Stakeholder consultation feedback log

- Concept-level Risk Assessment

Stage 3 – Spatial Coordination

Objective: Resolve all spatial, access and interface issues.

Mandatory Deliverables to Pass Gate

- Coordinated plant room / location drawings

- Cable routing and containment proposals

- Access, delivery and temporary works strategy

- Fire compartmentation and ventilation impact assessment

- Updated Risk Register and Method Statements reflecting spatial constraints

- Confirmation that existing infrastructure can support the new units (structural, electrical, thermal)

Stage 4 – Technical Design

Objective: Produce a complete, coordinated and fully compliant design package ready for procurement and installation.

Mandatory Deliverables to Pass Gate

- Full Technical Design Package (detailed drawings, schematics, specifications)

- Design calculations (short-circuit, discrimination, voltage drop, battery autonomy)

- Complete UPS and battery specifications compliant with BS 7671 and SHTM 06-01

- Detailed Installation Method Statements, LOTO procedures and RAMS

- Compliance Matrix (mapping against BS 7671, SHTM 06-01/06-02, Electricity at Work Regulations 1989, CDM 2015)

- Pre-Construction Information (CDM)

- Tender or direct-award procurement package

- Updated Programme and Resource Plan

- Design Risk Assessment signed by the Designer

Stage 5 – Manufacturing and Construction

Objective: Procure, manufacture, deliver, install and progressively test under controlled weekend working.

Mandatory Deliverables to Pass Gate (progressive; final package at end of Stage 5)

- Manufacturer drawings and Factory Acceptance Test (FAT) reports

- Delivery and secure storage records

- Approved Construction Phase Plan / Method Statements for each weekend

- Permit-to-Work and Isolation Certificates for every switch-out

- Daily and weekend progress / test records

- Temporary power and reinstatement records after each weekend

- Progressive as-installed drawings

- Evidence of dual-crew supervision and full LOTO compliance when two systems run concurrently

- Snagging list and resolution tracker

Stage 6 – Handover

Objective: Prove the systems are fully operational, safe, documented and ready for clinical use.

Mandatory Deliverables to Pass Gate (Practical Completion / Acceptance to Service)

- Electrical Installation Certificate(s) (EIC) issued under BS 7671

- Full Commissioning and Validation Reports (load-bank tests, transfer tests, autonomy, alarms, BMS integration)

- As-built drawings and single-line diagrams

- Complete Operation & Maintenance (O&M) Manuals (including configuration files and recommended spares)

- Battery installation and compliant disposal records (WEEE)

- Training records for Estates and relevant clinical staff

- Final Risk Assessment and closed-out RAMS

- Asset data uploaded to CAFM / asset register

- Formal “Acceptance to Service” certificate signed by NHS Forth Valley

- Defects Liability Schedule

Stage 7 – Use

Objective: Monitor performance and close out defects.

Mandatory Deliverables

- Defects Liability monitoring reports

- Final Lessons Learned report

- Updated Planned Preventative Maintenance (PPM) schedules

- End-of-Defects Certificate (if applicable)

4. Compliance & Regulatory Framework

All stages must demonstrate compliance with the following core requirements:

| Regulation / Standard | Key Application |
| --- | --- |
| BS 7671 (IET Wiring Regulations) | Design, installation, inspection and testing – EIC required at Stage 6 |
| SHTM 06-01 (Electrical Services Supply & Distribution) | UPS design, categories of supply, commissioning and validation |
| SHTM 06-02 (Electrical Safety – LV Systems) | Safe systems of work, permits-to-work, isolation procedures |
| Electricity at Work Regulations 1989 | Safe working on electrical systems |
| Health and Safety at Work etc. Act 1974 | General duties |
| Construction (Design and Management) Regulations 2015 | Designer and contractor duties (where applicable) |
| Building (Scotland) Regulations | Any structural, fire or energy implications |
| BS 7671 Section 710 | Additional requirements if medical locations are affected |
| WEEE Regulations | Battery disposal |
| NHS Forth Valley local policies | Estates procedures, HAI-SCRIBE, medical devices, Authorising Engineer protocols |

A live Compliance Matrix is maintained from Stage 4 onwards and forms part of the Stage 6 handover pack.

5. High-Level Programme Logic

- Stages 0–1: Baseline and briefing

- Stage 2: Concept approval (key go/no-go point)

- Stages 3–4: Design development and technical package

- Procurement / manufacturing lead time (variable – critical path item)

- Stage 5: Installation over 3–4 weekends (maximum 2 systems concurrent)

- Stage 6: Final commissioning and formal handover

- Stage 7: Defects period (typically 12 months)

Exact weekend dates will be fixed once UPS delivery dates are confirmed. Contingency weekends are retained in the programme.

6. Governance & Key Roles

- Project Sponsor: NHS Forth Valley Estates Director (or nominated deputy)

- Authorised Person (LV): Day-to-day electrical safety and progressive sign-off

- Authorising Engineer (AE): Independent advice and formal validation (recommended at Stages 4 and 6)

- Principal Designer: Design compliance and CDM duties

- Principal Contractor / Specialist Installer: Installation, testing and issue of EIC

- Commissioning Lead: System proving (OEM or independent)

7. Success Criteria at Stage 6 (Practical Completion)

- All 12 UPS units installed, fully commissioned and operating within specification

- Complete certification package issued (EIC, commissioning reports, O&M)

- Zero unplanned impact on clinical services during switch-overs

- Training completed and recorded

- Assets fully registered in CAFM with updated PPM

- Formal Acceptance to Service signed by NHS Forth Valley