High-Level Responsibility Chart for Project Managers
All 18 Systems – Mandatory Governance Roles

This is a practical summary of the mandatory roles that Project Managers must actively manage. It focuses on the people/groups who hold formal compliance, safety or statutory responsibility (not the day-to-day design or construction team).

1. Core Mandatory Roles Overview

| Role | Main Systems Affected | Typical Mandatory Actions | Key RIBA Stages |
| --- | --- | --- | --- |
| Water Safety Group (WSG) | Domestic Hot & Cold Water, LTHW / Boilers, Chilled Water, Steam (if water treatment involved), Drainage | Formal SBAR review & written approval; acceptance of Water Safety Plan / Written Scheme | Stage 1 (awareness), Stage 4 (formal approval), Stage 6 (handover) |
| Ventilation Safety Group (VSG) / IPC | Ventilation, Ward/Theatre Refurbishment, any system affecting air quality | Design review, SBAR/equivalent approval, validation acceptance | Stage 1–2, Stage 4, Stage 6 |
| Medical Gas Safety Group (MGSG) + Authorised Person (MGPS) | Medical Gases (including Pendants) | Design approval, Permit-to-Work control, validation & formal handover sign-off | Stage 1, Stage 4, Stage 5–6 |
| Authorising Engineer (AE) | Electrical, Medical Gases, Lifts, sometimes Fire & Water | Independent review, appointment of APs, audit of systems, formal sign-off | Stage 4 (design), Stage 6 (handover) |
| Authorised Person (AP) | Electrical, Medical Gases, sometimes Water / Steam | Day-to-day control, isolation, Permit-to-Work, operational acceptance | Stage 5–6 |
| Competent Person (PSSR / LOLER) | Steam, Non-medical Compressed Air, Lifts, Pressure systems | Written Scheme of Examination, statutory inspections, certification | Stage 4 (design), Stage 6–7 |
| Fire Safety Advisor / AE (Fire) | Fire Detection & Alarm, Fire Suppression, Lifts (firefighting/escape), Ward/Theatre Refurb | Fire strategy compliance, design review, cause & effect approval | Stage 2–4, Stage 6 |
| PFI Board / NHS (Cost Approval) | All 18 systems | Formal lifecycle / cost approval of quotes + contingency | Stage 4 Pre-Contract Hold Point |
| Clinical / Soft FM Stakeholders | Ward/Theatre Refurb, Nurse Call, Medical Gases, Ventilation, Lifts | User acceptance, operational readiness | Stage 4 & Stage 6 |

2. Simplified RACI-Style View for Project Managers

(Focus on Mandatory Approvals only)

| Mandatory Deliverable | Responsible (does the work) | Accountable (signs off) | Consulted | Informed |
| --- | --- | --- | --- | --- |
| Pre-Contract Cost Approval (min. 2 quotes + contingency) | Project Manager / Cost Consultant | PFI Board / NHS | Design Team, Estates | Contractor (after approval) |
| SBAR / Formal Risk Submission (Water) | Design Team / Project Manager | Water Safety Group (WSG) | IPC, Estates | All project team |
| SBAR / Formal Risk Submission (Ventilation) | Design Team / Project Manager | VSG / IPC | Estates, Clinical | All project team |
| MGPS Design & Handover Approval | Design Team + Specialist Contractor | MGSG + Authorised Person (MGPS) | AE (MGPS) | Clinical users |
| Electrical System Acceptance | Design Team + Contractor | Authorising Engineer (Electrical) + AP | Estates | Clinical |
| Lift Thorough Examination / Acceptance | Specialist Lift Contractor | Competent Person + AE (Lifts) | Estates | — |
| Fire System Cause & Effect / Acceptance | Design Team + Contractor | Fire Safety Advisor / AE (Fire) | Estates | — |
| Pressure Systems Written Scheme | Design Team / Specialist | Competent Person (PSSR) | AE if appointed | Estates |
| Final Handover / Practical Completion | Project Manager + Contractor | Client / Estates + relevant Safety Group | All AEs/APs | Soft FM / Clinical |

3. Quick Project Manager Checklist – “Who Must Sign Before We Can Proceed?”

| Gate | What must be in place before moving forward |
| --- | --- |
| End of Stage 3 / Start of Stage 4 | Early engagement with relevant Safety Group(s) recorded |
| Stage 4 Pre-Contract Hold Point | • Min. 2 quotes + contingency submitted • Formal SBAR to the relevant Safety Group • Written approval from Safety Group • Written cost approval from PFI Board / NHS |
| Before Stage 5 starts | Contractor appointed only after the above approvals |
| Before Handover (Stage 6) | Relevant AE / AP / Competent Person / Safety Group formal acceptance |
| Before Practical Completion | All statutory certificates + updated Written Schemes / Water Safety Plan / Ventilation arrangements |

4. Recommendation for Project Managers

Create a simple one-page “Mandatory Approvals Tracker” for each project that lists:

- Which Safety Group / AE / AP applies to this specific system

- The exact Stage 4 Hold Point requirements

- Named individuals and target dates for their formal written approval

This keeps the detailed 18 checklists for the technical teams, while giving Project Managers a clear, high-level view of the non-negotiable governance steps.