Deliverables Checklist Replacement / Upgrade of Domestic Hot & Cold Water Systems in a Hospital Aligned to RIBA Plan of Work 2020 & relevant SHTMs

It is intended for projects involving the replacement, major upgrade or significant modification of Domestic Hot and Cold Water Systems in hospital premises (storage, distribution, pumping, temperature control, TMVs, monitoring and associated water safety measures).

Primary SHTM / Guidance References

| System Element | Key Guidance |
| --- | --- |
| Domestic Hot & Cold Water Systems | SHTM 04-01 – Water safety (Parts A, B, C, D, E, F & G) |
| Overarching | SHTM 00 – Policies and principles |
| Linked Systems | SHTM 03-01 (Ventilation – if linked), SHTM 06 series (Electrical power to pumps/controls), SHTM 08-03 (Bedhead services – TMVs), BMS interfaces |
| Core Standards | HSE ACOP L8 & HSG 274, BS EN 806, BS 8558, Water Supply (Water Fittings) Regulations / Scottish Water Byelaws, CDM 2015 |

Key Principles

- Control of Legionella and other waterborne pathogens is paramount.

- Water Safety Group (WSG) engagement and approval is required at key stages.

- Continuity of hot and cold water supply to clinical areas must be maintained during the works.

- Temperature control, stagnation prevention, material selection and monitoring are critical.

- Full compliance with SHTM 04-01 is expected for both design and operational management.

Stage 0 – Strategic Definition

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Business case / need identification (system age, Legionella risk, temperature performance, resilience, water quality) |  | SHTM 00, SHTM 04-01 |
| Strategic brief & project outcomes (patient safety, Legionella control, continuity of supply, energy efficiency) |  | SHTM 00 |
| High-level clinical / operational impact assessment |  | SHTM 00, SHTM 04-01 |

Stage 1 – Preparation and Briefing

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Project Brief (scope of hot & cold water works, temperature regime, TMV strategy, monitoring requirements) |  | SHTM 00, SHTM 04-01 |
| Existing system condition surveys (storage, distribution, pumps, calorifiers, TMVs, dead legs, water quality baseline) |  | SHTM 04-01 Part A & B |
| Water risk assessment review and gap analysis |  | SHTM 04-01, HSE L8 |
| Initial risk register (Legionella, loss of supply, temperature control, materials) |  | SHTM 00, CDM, SHTM 04-01 |
| Project Execution Plan & procurement strategy |  | — |
| Formal engagement with Water Safety Group (WSG) |  | SHTM 04-01 |

Stage 2 – Concept Design

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Concept design options (storage vs instantaneous, central vs local, return systems, TMV strategy, monitoring) |  | SHTM 04-01 Part A |
| Outline water system strategy (temperatures, flow rates, resilience, stagnation prevention) |  | SHTM 04-01 Part A |
| Preliminary schematics and load/demand assessment |  | SHTM 04-01 |
| Outline specifications & preliminary cost plan |  | — |
| Design risk assessment (including Legionella) |  | CDM, SHTM 00, SHTM 04-01 |

Stage 3 – Spatial Coordination

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Coordinated design (plant locations, pipe routes, storage vessels, pump rooms, access for maintenance) |  | SHTM 04-01 Part A |
| Spatial coordination with structure, electrical, ventilation and other services |  | SHTM 00 |
| Updated cost plan, risk register & high-level phasing / temporary supply strategy |  | — |
| Confirmation of temperature monitoring and sampling point strategy |  | SHTM 04-01 |

Stage 4 – Technical Design

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Full technical design drawings, schematics and pipework layouts |  | SHTM 04-01 Part A |
| Detailed specifications (pipework materials, storage vessels, calorifiers/heat exchangers, pumps, TMVs, valves, insulation, controls) |  | SHTM 04-01 Part A, BS EN 806 |
| Water treatment / chemical dosing / temperature control strategy |  | SHTM 04-01 Part A |
| Legionella control measures and schematic risk assessment update |  | SHTM 04-01, HSE L8 |
| Temperature monitoring, sampling points and BMS integration design |  | SHTM 04-01 |
| Electrical design associated with pumps and controls |  | SHTM 06 series |
| Building Regulations / Water Byelaws compliance information |  | Scottish Water Byelaws |
| Pre-construction information & input to Construction Phase Plan |  | CDM |
| Designer’s Risk Assessment & residual risks |  | CDM, SHTM 04-01 |
| Tender documentation / Scope of Works / pricing schedules |  | — |
| Water Safety Group review and approval of design |  | SHTM 04-01 |

Stage 5 – Manufacturing and Construction

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Contractor method statements, detailed phasing & temporary water supply arrangements |  | Critical for continuity |
| Material & equipment certificates (pipework, fittings, vessels, TMVs – WRAS approved where required) |  | SHTM 04-01, Water Byelaws |
| Installation of pipework, storage, pumps, TMVs, insulation and controls |  | SHTM 04-01 Part A |
| Jointing, flushing, cleaning and disinfection records |  | SHTM 04-01 Part D |
| Water sampling and microbiological testing records (pre- and post-disinfection) |  | SHTM 04-01 Parts C & D |
| Progress records, quality inspections, change control log |  | — |
| Temporary supply / hybrid working arrangements (if phased) |  | Essential |
| Decommissioning & strip-out records of redundant water systems |  | SHTM 04-01 |

Stage 6 – Handover

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Full commissioning & validation records (temperatures, flow rates, pressures, TMV performance, pump duties) |  | SHTM 04-01 Part A |
| Final disinfection and microbiological clearance certificates |  | SHTM 04-01 Part D |
| Temperature profiling and balancing records |  | SHTM 04-01 |
| As-fitted drawings, schematics, valve schedules and sampling point registers |  | SHTM 04-01 Part A |
| Comprehensive O&M manuals, including Written Scheme of Control |  | SHTM 04-01 Part B & G |
| Updated Health & Safety File |  | CDM |
| Training & demonstration records for estates and clinical staff |  | SHTM 04-01 Part B |
| Residual risk register |  | CDM |
| Practical Completion / handover certificate |  | — |
| Formal Water Safety Group acceptance and updated Water Safety Plan |  | SHTM 04-01 |

Stage 7 – Use

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Soft landings / post-occupancy review (temperature performance, water quality, user feedback) |  | SHTM 00 |
| Updated Water Safety Plan / Written Scheme of Control |  | SHTM 04-01 Parts B & G |
| Ongoing monitoring, sampling and maintenance regime |  | SHTM 04-01 Part B |
| Defects liability records & final account |  | — |
| Lessons learned report |  | SHTM 00 |

Cross-Stage / Continuous Deliverables

- Live Health & Safety File

- Project risk register (updated at each stage)

- Change control log

- Water Safety Group (WSG) engagement and formal approvals at key gateways

- Maintenance of continuous hot and cold water supply to clinical areas throughout the works

- Evidence of compliance with SHTM 04-01, HSE ACOP L8 / HSG 274 and Water Byelaws

- Full traceability of materials and water quality records