Deliverables Checklist Replacement / Upgrade of Fume Cupboards in a Hospital Aligned to RIBA Plan of Work 2020 & relevant Standards

This checklist follows the exact same format as the other Hard FM system checklists. It is intended for projects involving the installation, replacement or major upgrade of fume cupboards in hospital premises (laboratory, pathology and pharmacy fume cupboards, ducted and recirculating units, associated extract ductwork, and control systems).

Primary Guidance References

| System Element | Key Guidance |
| --- | --- |
| Fume Cupboards | BS EN 14175 (all parts - design, performance and testing of ducted fume cupboards) SHTM 03-01 (extract ventilation, where linked) |
| Local Exhaust Ventilation (LEV) | COSHH Regulation 9 - thorough examination and test at least every 14 months (shorter intervals for higher-risk substances per Schedule 4 or risk assessment) HSE HSG258 guidance |
| Supporting | DSEAR (where flammable solvents are handled) SHTM 06 series (electrical/controls) CDM 2015 |
| Core Standards | BS EN 14175, COSHH 2002 (as amended), HSG258, DSEAR 2002 (amended 2015) |

Key Principles

- Minimum face velocity of 0.4 m/s across the sash opening, with no more than ±20% variance, must be maintained and demonstrated - not assumed from manufacturer literature alone.

- LEV thorough examination and test (COSHH Regulation 9) at least every 14 months is a statutory minimum, not a target - shorter intervals apply for higher-risk substances per Schedule 4 or local risk assessment.

- Where flammable solvents are used, a DSEAR risk assessment is required alongside COSHH - the two are complementary, not interchangeable.

- Continuity of laboratory, pathology or pharmacy service during the works must be maintained, or a validated interim arrangement provided.

- Extract ductwork integrity and discharge point location (relative to fresh-air intakes and occupied areas) must be verified, not assumed unchanged from the original installation.

Stage 0 – Strategic Definition

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Business case / need identification (cupboard condition, face-velocity performance, LEV test history, capacity) |  | COSHH Reg 9 |
| Strategic brief & project outcomes (containment performance, continuity of lab service, energy efficiency) |  | SHTM 00 |
| High-level clinical / operational impact assessment (affected lab/pathology/pharmacy services) |  | SHTM 00 |
| Confirmation of which substances/processes the cupboard(s) serve (COSHH/DSEAR relevance) |  | COSHH, DSEAR |

Stage 1 – Preparation and Briefing

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Project Brief (scope of cupboards, ducted vs recirculating, capacity, substance/process inventory) |  | COSHH |
| Existing condition surveys including face-velocity and LEV thorough examination/test history |  | BS EN 14175, COSHH Reg 9 |
| Substance/process inventory review (flammable solvents, DSEAR-relevant materials) |  | DSEAR |
| Initial risk register (loss of containment, service continuity, DSEAR/flammable-substance risk) |  | COSHH, DSEAR, CDM |
| Project Execution Plan & procurement strategy |  |  |
| Engagement with Laboratory, Pathology, Pharmacy, H&S and Estates |  | Essential |
| Confirmation of ducted versus recirculating type for each unit |  | BS EN 14175 |

Stage 2 – Concept Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Concept design options (ducted vs recirculating, constant-air-volume vs variable-air-volume control) |  | BS EN 14175 |
| Outline extract strategy including discharge point location relative to intakes/occupied areas |  | SHTM 03-01 |
| Preliminary layout and containment strategy |  |  |
| Outline specifications & preliminary cost plan |  |  |
| Design risk assessment |  | CDM |
| DSEAR screening for any flammable solvents used at the cupboard(s) |  | DSEAR |

Stage 3 – Spatial Coordination

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Coordinated design (ductwork routes, discharge point, extract fan plant space, access for maintenance) |  |  |
| Spatial coordination with structure, fire compartments and other services |  | SHTM 00 |
| Updated cost plan, risk register & high-level phasing / temporary lab-service strategy |  |  |
| Confirmation of continuity strategy for laboratory/pathology/pharmacy service during the works |  | Essential |

Stage 4 – Technical Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full technical design drawings and extract ductwork schematics |  | BS EN 14175 |
| Detailed specifications (cupboard, extract fan, controls, VAV system if applicable) |  | BS EN 14175 |
| Face-velocity and containment design confirmation (0.4 m/s ±20%) |  | BS EN 14175 |
| DSEAR risk assessment finalised where flammable solvents are used |  | DSEAR |
| Electrical and controls design |  | SHTM 06 series |
| Building Regulations / statutory compliance information |  |  |
| Pre-construction information & input to Construction Phase Plan |  | CDM |
| Designer’s Risk Assessment & residual risks |  | CDM |
| Tender documentation / Scope of Works / pricing schedules |  |  |
| Stakeholder review and approval of design (Laboratory, Pathology, Pharmacy, H&S) |  | Essential |
| Obtain minimum of two competitive quotations |  | Critical commercial requirement |
| Submit quotations, cost comparison and recommendation to PFI Board / NHS for lifecycle approval |  |  |
| PRE-CONTRACT HOLD POINT: No contractor appointment and no further progression until written cost approval is received |  | Clear commercial & governance cut-off |

Stage 5 – Manufacturing and Construction

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Contractor method statements, detailed phasing & temporary lab-service arrangements |  | Critical for lab service |
| Material & equipment certificates (cupboard, extract fan, ductwork, controls) |  | Manufacturer |
| Installation of cupboard(s), ductwork, extract fan and controls |  |  |
| Commissioning face-velocity and containment testing |  | BS EN 14175 |
| Progress records, quality inspections, change control log |  |  |
| Temporary lab-service arrangements (if phased) |  | Essential |
| First LEV thorough examination and test (COSHH Regulation 9) |  | HSG258 |
| Decommissioning & disposal records of redundant unit |  |  |

Stage 6 – Handover

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full commissioning records including LEV thorough examination and test certificate |  | COSHH Reg 9, HSG258 |
| Face-velocity verification across sash positions |  | BS EN 14175 |
| As-fitted drawings, ductwork schematics and control system configuration records |  |  |
| Comprehensive O&M manuals |  | SHTM 00 |
| Updated Health & Safety File |  | CDM |
| Training & demonstration records for laboratory/estates staff |  | SHTM 00 |
| Residual risk register |  | CDM |
| Practical Completion / handover certificate |  |  |
| Formal client / stakeholder acceptance |  |  |
| Confirmation of ongoing 14-month LEV thorough examination/test schedule established |  | COSHH Reg 9 |
| DSEAR risk assessment filed with Estates/H&S |  | DSEAR |

Stage 7 – Use

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Soft landings / post-occupancy review (containment performance, user feedback, energy use) |  | SHTM 00 |
| Ongoing LEV thorough examination and test regime in operation (at least every 14 months) |  | COSHH Reg 9, HSG258 |
| Periodic face-velocity spot-checks |  | BS EN 14175 |
| Defects liability records & final account |  |  |
| Lessons learned report |  | SHTM 00 |

Cross-Stage / Continuous Deliverables

- Live Health & Safety File

- Project risk register (updated at each stage)

- Change control log

- Stakeholder engagement (Laboratory, Pathology, Pharmacy, H&S, Estates) at key gateways

- Maintenance of continuity of laboratory, pathology or pharmacy service throughout the works

- Evidence of compliance with BS EN 14175, COSHH and manufacturer requirements

- LEV thorough examination and test records maintained on a rolling maximum-14-month cycle

- Evidence of current PVG Scheme membership for all contractor personnel attending site

- Where works are in, adjacent to, above or below a room housing ionising-radiation imaging equipment (CT, X-ray, fluoroscopy, nuclear medicine): confirm Radiation Protection Adviser (RPA) sign-off on shielding integrity per the Room/Ward/Theatre Refresh checklist - a separate gate from HAI-SCRIBE, not covered by it