Deliverables Checklist Replacement / Upgrade of Fire Curtains in a Hospital Aligned to RIBA Plan of Work 2020 & relevant Standards

This checklist follows the exact same format as the other Hard FM system checklists. It is intended for projects involving the installation, replacement or major upgrade of active fire curtain barrier assemblies in hospital premises (smoke/fire curtains at compartment lines, atria, and where used as part of a wider smoke control strategy).

Primary Guidance References

| System Element | Key Guidance |
| --- | --- |
| Fire Curtains | BS 8524 Part 1 (specification) and Part 2 (code of practice for application, installation and maintenance) Fire (Scotland) Act 2005 Part 3, Fire Safety (Scotland) Regulations 2006 |
| Certification status | BS 8524's own third-party certification scheme lapsed in June 2023; BS EN 16034 is now the only harmonised CE-marking route for the underlying doorset/barrier product - confirm current certification status with the manufacturer/installer at time of works, do not assume BS 8524 third-party certification is still current |
| Supporting | SHTM 82/85 (fire detection and general fire precautions, where the curtain interfaces with the fire alarm system) SHTM 03-01 (where linked to a smoke control system) CDM 2015 |
| Core Standards | BS 8524-1, BS 8524-2, BS EN 16034 |

Key Principles

- Where a fire curtain forms part of a wider smoke control system, it must be tested in conjunction with that system, at least quarterly (BS 8524).

- A gravity failsafe and backup power for retract facilities are safety-critical features and must be verified as part of commissioning, not assumed present.

- The current certification status of the specific product should be confirmed directly with the manufacturer before specification, given BS 8524's own third-party certification scheme lapsed in 2023 - do not assume from the standard's name alone.

- Continuity of the affected compartment/escape route's fire strategy must be maintained throughout the works (temporary fire-stopping/watch arrangements where needed).

Stage 0 – Strategic Definition

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Business case / need identification (curtain condition, test history, fire strategy relevance) |  | SHTM 82 |
| Strategic brief & project outcomes (compartmentation integrity, smoke control interface) |  | SHTM 00 |
| High-level clinical / operational impact assessment (affected compartment/escape route) |  | SHTM 00 |
| Confirmation of whether the curtain forms part of a wider smoke control system |  | BS 8524 |

Stage 1 – Preparation and Briefing

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Project Brief (scope of curtain(s), location, fire strategy role) |  | SHTM 00 |
| Existing condition survey including current certification status of the installed product |  | BS 8524 |
| Fire strategy review (compartmentation, escape routes, smoke control interface) |  | SHTM 82, SHTM 85 |
| Initial risk register (loss of compartmentation, smoke control failure, fire strategy impact) |  | SHTM 00, CDM |
| Project Execution Plan & procurement strategy |  |  |
| Engagement with Fire Safety Advisor and Estates |  | Essential |
| Confirmation of interface with fire alarm/smoke control system |  | SHTM 82 |

Stage 2 – Concept Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Concept design options (curtain type, headbox location, drop sequence) |  | BS 8524 |
| Outline fire-curtain strategy (location, fail-safe, interface with smoke control system) |  | BS 8524 |
| Preliminary layout |  |  |
| Outline specifications & preliminary cost plan |  |  |
| Design risk assessment |  | CDM |
| Confirmation of current BS EN 16034 certification route for shortlisted products |  | BS EN 16034 |

Stage 3 – Spatial Coordination

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Coordinated design (curtain location, headbox, guide rails, structural fixing) |  |  |
| Spatial coordination with structure, ceilings, other services and fire compartments |  | SHTM 00 |
| Updated cost plan, risk register & high-level phasing strategy |  |  |
| Confirmation of temporary fire-stopping / fire-watch strategy during the works |  | Essential |

Stage 4 – Technical Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full technical design drawings |  | BS 8524 |
| Detailed specifications (curtain, headbox, controls, gravity failsafe, backup power) |  | BS 8524 |
| Fire-alarm / smoke-control interface design |  | SHTM 82, SHTM 03-01 |
| Electrical and controls design |  | SHTM 06 series |
| Building Regulations / statutory compliance information |  | Fire (Scotland) Act 2005 |
| Pre-construction information & input to Construction Phase Plan |  | CDM |
| Designer’s Risk Assessment & residual risks |  | CDM |
| Tender documentation / Scope of Works / pricing schedules |  |  |
| Fire Safety Advisor and stakeholder review and approval of design |  | Essential |
| Obtain minimum of two competitive quotations |  | Critical commercial requirement |
| Submit quotations, cost comparison and recommendation to PFI Board / NHS for lifecycle approval |  |  |
| PRE-CONTRACT HOLD POINT: No contractor appointment and no further progression until written cost approval is received |  | Clear commercial & governance cut-off |

Stage 5 – Manufacturing and Construction

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Contractor method statements, detailed phasing & temporary fire-stopping arrangements |  | Critical for fire strategy |
| Material & equipment certificates including current certification evidence |  | BS 8524, BS EN 16034 |
| Installation of curtain, headbox, guide rails and controls |  |  |
| Gravity failsafe and backup power testing during installation |  | BS 8524 |
| Progress records, quality inspections, change control log |  |  |
| Temporary fire-stopping arrangements (if phased) |  | Essential |
| Commissioning of quarterly-test regime where linked to a smoke control system |  | BS 8524 |
| Decommissioning & disposal records of redundant curtain |  |  |

Stage 6 – Handover

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full commissioning records (drop test, gravity failsafe, backup power verification) |  | BS 8524 |
| Quarterly joint-test-with-smoke-control-system verification, where applicable |  | BS 8524 |
| As-fitted drawings and control system configuration records |  |  |
| Comprehensive O&M manuals |  | SHTM 00 |
| Updated Health & Safety File |  | CDM |
| Training & demonstration records for estates staff |  | SHTM 00 |
| Residual risk register |  | CDM |
| Practical Completion / handover certificate |  |  |
| Formal client / Fire Safety Advisor acceptance |  | Essential |
| Confirmation of ongoing test regime established |  | BS 8524 |
| Current certification evidence for the installed product filed with Estates |  | BS 8524, BS EN 16034 |

Stage 7 – Use

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Soft landings / post-occupancy review (reliability, fire strategy performance) |  | SHTM 00 |
| Ongoing quarterly test regime in operation, where the curtain forms part of a smoke control system |  | BS 8524 |
| Periodic drop-test and failsafe verification |  | BS 8524 |
| Defects liability records & final account |  |  |
| Lessons learned report |  | SHTM 00 |

Cross-Stage / Continuous Deliverables

- Live Health & Safety File

- Project risk register (updated at each stage)

- Change control log

- Stakeholder engagement (Fire Safety Advisor, Estates) at key gateways

- Maintenance of fire strategy and compartmentation integrity throughout the works

- Evidence of compliance with BS 8524 and manufacturer requirements

- Ongoing quarterly test regime (where the curtain forms part of a smoke control system) and periodic drop-test/failsafe verification records

- Evidence of current PVG Scheme membership for all contractor personnel attending site

- Where works are in, adjacent to, above or below a room housing ionising-radiation imaging equipment (CT, X-ray, fluoroscopy, nuclear medicine): confirm Radiation Protection Adviser (RPA) sign-off on shielding integrity per the Room/Ward/Theatre Refresh checklist - a separate gate from HAI-SCRIBE, not covered by it