Deliverables Checklist
Replacement of Medical Gas Systems (including Pendants) in a Hospital
Aligned to RIBA Plan of Work 2020 & relevant SHTMs

Primary SHTM / Guidance References

| System Element | Key Guidance |
| --- | --- |
| Medical Gas Pipeline Systems | SHTM 02-01 Part A – Design, installation, validation and verification SHTM 02-01 Part B – Operational management |
| Overarching / Electrical | SHTM 00, SHTM 06-01 |
| Supporting | Medical Gas Safety Group (MGSG), Permit-to-Work system, Authorised Person (MGPS) / Competent Person roles, BS EN ISO 7396-1, BS EN ISO 9170, BS EN ISO 11197, CDM 2015 |

Key Principles

- Patient safety is paramount (identity, continuity, quality and quantity of supply).

- All works must be controlled via the Permit-to-Work system and overseen by the Authorised Person (MGPS).

- Continuity of medical gas supply to clinical areas must be maintained.

- Pendants are treated as medical supply units and must comply with SHTM 02-01 and BS EN ISO 11197.

Key Governance Rule
A clear Pre-Contract Hold Point exists inside Stage 4.
No contractor appointment and no Stage 5 works may proceed until:

- Minimum two competitive quotes have been obtained (with contingency), and

- Formal lifecycle/cost approval has been received from the PFI Board or NHS, and

- Written approval of the SBAR (or equivalent formal submission) has been received from the Medical Gas Safety Group / Authorised Person (MGPS).

Stage 0 – Strategic Definition

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Business case / need identification (system age, compliance, clinical risk, pendant condition) |  | SHTM 00, SHTM 02-01 |
| Strategic brief & project outcomes (continuity of supply, patient safety, resilience) |  | SHTM 00 |
| High-level clinical / operational impact assessment |  | SHTM 00, MGSG |

Stage 1 – Preparation and Briefing

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Project Brief (scope of MGPS / pendant replacement, continuity requirements) |  | SHTM 00, SHTM 02-01 |
| Existing system condition surveys (pipework, terminal units, pendants, plant, alarms) |  | SHTM 02-01 Part B |
| Baseline identity, quality and flow testing records |  | SHTM 02-01 Part A |
| Initial risk register (isolation risks, cross-connection, pendant structural loads) |  | SHTM 00, CDM, MGSG |
| Project Execution Plan & procurement strategy |  | — |
| Early engagement with Medical Gas Safety Group (MGSG) and Authorised Person (MGPS) |  | SHTM 02-01 |

Stage 2 – Concept Design

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Concept design options (phased replacement, temporary gas supplies, pendant strategy) |  | SHTM 02-01 Part A |
| Outline MGPS strategy (sources of supply, distribution, terminal units, pendants, AGSS) |  | SHTM 02-01 Part A |
| Preliminary pendant / medical supply unit selection and locations |  | SHTM 02-01, BS EN ISO 11197 |
| Outline specifications & preliminary cost plan |  | — |
| Design risk assessment |  | CDM, SHTM 00, SHTM 02-01 |

Stage 3 – Spatial Coordination

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Coordinated design (pipe routes, plant locations, pendant positions, structural supports) |  | SHTM 02-01 Part A |
| Spatial coordination with structure, electrical, data, lighting and other services |  | SHTM 06-01 |
| Updated cost plan, risk register & high-level phasing / isolation strategy (principles only) |  | — |
| Confirmation of temporary supply arrangements |  | SHTM 02-01 |

Stage 4 – Technical Design

(Contains the Pre-Contract Hold Point)

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Developed design / performance specifications (sufficient for accurate pricing) |  | Not full construction-issue drawings |
| Detailed Scope of Works |  | Clear boundaries |
| Updated cost plan including appropriate contingency |  | Realistic budget envelope |
| Structural design information for pendant supports / ceiling fixings |  | — |
| Electrical & data design associated with pendants |  | SHTM 06-01 |
| Alarm system design and interface requirements |  | SHTM 02-01 Part A |
| Building Regulations / statutory compliance information |  | — |
| Designer’s Risk Assessment & residual risks |  | CDM, SHTM 02-01 |
| Pre-construction information & input to Construction Phase Plan |  | CDM |
| Tender documentation / Scope of Works / pricing schedules |  | — |
| Obtain minimum of two competitive quotations |  | Critical commercial requirement |
| Prepare and submit formal SBAR (or equivalent) to the Medical Gas Safety Group / Authorised Person (MGPS) |  | SHTM 02-01 |
| Obtain written MGSG / AP (MGPS) approval |  | — |
| Submit quotations, cost comparison, contingency and recommendation to PFI Board / NHS for lifecycle approval |  | — |
| PRE-CONTRACT HOLD POINT: No contractor appointment and no further progression until written PFI/NHS cost approval and MGSG/AP approval are both received |  | Clear commercial & governance cut-off |
| After approval and contractor appointment: complete full technical drawings, final coordination and any remaining design details |  | Post-appointment activity still recorded under Stage 4 |

Stage 5 – Manufacturing and Construction

(Only after Stage 4 Hold Point is cleared and contractor is onboarded)

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Contractor’s detailed Method Statements, full RAMS, detailed phasing, isolation & Permit-to-Work procedures |  | Only after appointment – SHTM 02-01 Part B |
| Temporary medical gas supply arrangements (if required) – design, installation & validation |  | SHTM 02-01 Part A |
| Material & equipment certificates (pipework, fittings, terminal units, pendants, plant) |  | SHTM 02-01 Part A |
| Installation of new pipeline systems, valves, AVSUs and terminal units |  | SHTM 02-01 Part A |
| Installation of ceiling pendants / medical supply units (including structural fixings, gas hoses, electrical & data) |  | SHTM 02-01, BS EN ISO 11197 |
| Brazing / jointing records (oxygen-free nitrogen purged, fluxless) |  | SHTM 02-01 Part A |
| Pressure testing, leakage testing and purity / identity testing records |  | SHTM 02-01 Part A |
| Alarm system installation and testing |  | SHTM 02-01 Part A |
| Electrical installation & test certificates associated with pendants (BS 7671) |  | SHTM 06-01 |
| Progress records, quality inspections, change control log & Permit-to-Work records |  | SHTM 02-01 Part B |
| Decommissioning & strip-out records of redundant MGPS / pendants |  | SHTM 02-01 |

Stage 6 – Handover

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Full validation and verification records (carcass, system, performance) |  | SHTM 02-01 Part A |
| Identity, quality, flow and pressure test certificates for all gases and vacuum |  | SHTM 02-01 Part A |
| Pendant performance tests (movement, braking, hose integrity, terminal unit function) |  | SHTM 02-01, manufacturer requirements |
| As-fitted drawings & schematics (including terminal unit schedules and pendant locations) |  | SHTM 02-01 Part A |
| Comprehensive O&M manuals (including pendant maintenance and hose life policy) |  | SHTM 02-01 Part B |
| Updated Health & Safety File |  | CDM |
| Training & demonstration records for Authorised Persons, Competent Persons and clinical users |  | SHTM 02-01 Part B |
| Residual risk register |  | CDM |
| Practical Completion / handover certificate |  | — |
| MGSG acceptance and formal handover of the MGPS |  | SHTM 02-01 |
| Temporary supply decommissioning records (if applicable) |  | SHTM 02-01 |

Stage 7 – Use

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Soft landings / post-occupancy review (system performance, pendant usability, alarm response) |  | SHTM 00 |
| Updated operational procedures, Permit-to-Work arrangements and Written Scheme |  | SHTM 02-01 Part B |
| Ongoing planned preventive maintenance regime (including pendant hose replacement schedule) |  | SHTM 02-01 Part B |
| Defects liability records & final account |  | — |
| Lessons learned report |  | SHTM 00 |

Cross-Stage / Continuous Deliverables

- Live Health & Safety File

- Project risk register (updated at each stage)

- Change control log

- Full Permit-to-Work records

- Medical Gas Safety Group (MGSG) and Authorised Person (MGPS) engagement and formal approvals at key gateways

- Evidence of compliance with manufacturer instructions for pendants, terminal units and plant

- Authorised Person (MGPS) oversight throughout design, installation, validation and handover