Deliverables Checklist Replacement / Upgrade of Building Fabric & External Envelope in a Hospital Aligned to RIBA Plan of Work 2020 & relevant Standards

This checklist follows the exact same format as the other Hard FM system checklists. It is intended for projects involving the replacement or major upgrade of a hospital's external building fabric and envelope (roofing, external wall cladding, external doors and windows), as distinct from internal fit-out works - see Room or Ward Refresh for internal finishes and furniture, which treats building services and fabric as interfaces rather than the system being replaced.

Primary Guidance References

| System Element | Key Guidance |
| --- | --- |
| Roofing | BS 6229:2025 (Flat roofs with continuously supported flexible waterproof coverings - Code of practice, superseding the 2018 edition) governs design, specification, construction and aftercare of flat/low-pitch roofs. |
| Thermal / weather performance | Building (Scotland) Regulations 2004 and the associated non-domestic Technical Handbook (Section 6, Energy) set minimum thermal and weathertightness performance for the replaced envelope. |
| Asbestos | Control of Asbestos Regulations 2012 - Regulation 4 (Duty to Manage) requires an asbestos survey before any refurbishment, and Regulation 7 requires all reasonably practicable asbestos-containing materials to be removed before major refurbishment or demolition; a fully intrusive Refurbishment & Demolition (R&D) survey is required, not a routine management survey. |
| Working at height | Work at Height Regulations 2005 governs fall-arrest, edge protection and safe access for all roof and high-level external envelope work. |

Key Principles

- A Refurbishment & Demolition (R&D) asbestos survey is a precondition of design, not a construction-phase task - Regulation 7 of CAR 2012 requires asbestos-containing materials to be removed as far as reasonably practicable before major refurbishment, which can materially change scope and programme if found late.

- Roof and envelope works above, adjacent to or over-sailing occupied clinical areas require the same continuity-of-service and containment discipline as an internal works package - weather protection, IPC dust/debris control and noise/vibration management must be designed in, not improvised on site.

- Where envelope works interface with a Renewable/Net Zero Plant project (roof-mounted PV, external wall insulation feeding a heat pump retrofit), structural loading and sequencing must be coordinated jointly - see Renewable & Net Zero Plant for the plant-specific deliverables this checklist does not duplicate.

- Work at Height Regulations 2005 fall-arrest and edge-protection provisions must be designed into the access strategy at Concept Design, not left to the contractor's method statement alone.

- Where scope is in, adjacent to, above or below a room housing ionising-radiation imaging equipment, structural or envelope disturbance can affect shielding integrity even without any M&E system being touched - the RPA cross-reference below applies to fabric-only projects too, not just system replacements.

Stage 0 – Strategic Definition

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Business case / need identification (envelope condition survey, water ingress history, thermal performance baseline) |  |  |
| Initial stakeholder map, including Estates, IPC and affected clinical departments below/adjacent to the works |  |  |
| Preliminary asbestos management-survey review of existing records |  | CAR 2012 |
| Expanded risk register |  | SHTM 00, CDM 2015 |

Stage 1 – Preparation and Briefing

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Project Brief (scope: roof area, cladding extent, doors/windows affected, phasing constraints) |  |  |
| Refurbishment & Demolition (R&D) asbestos survey commissioned and completed |  | CAR 2012 Reg 4 & 7 |
| Existing structural condition survey (roof deck, wall ties, external door/window frames) |  |  |
| Engagement with IPC and affected clinical departments on containment/weather-protection requirements |  |  |
| Working at height access strategy scoped |  | Work at Height Regulations 2005 |

Stage 2 – Concept Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Concept design options (roofing system type, cladding system, glazing performance) |  | BS 6229:2025 |
| Outline thermal/weathertightness performance targets |  | Building (Scotland) Regs 2004 |
| Outline coordination with any planned Renewable/Net Zero Plant works (roof loading, sequencing) |  | Renewable & Net Zero Plant checklist |

Stage 3 – Spatial Coordination

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Coordinated design (roof build-up, cladding fixings, door/window schedules, temporary weather protection) |  |  |
| Confirmed structural loading assessment where roof-mounted plant is proposed |  |  |
| Updated risk register incorporating asbestos survey findings |  |  |

Stage 4 – Technical Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full technical design drawings and specifications |  | BS 6229:2025 |
| Fall-arrest/edge-protection design finalised |  | Work at Height Regulations 2005 |
| Asbestos removal method statement and licensed-contractor arrangements where required |  | CAR 2012 |
| Thermal/weathertightness performance calculations confirming compliance |  | Building (Scotland) Regs 2004 |
| Radiation Protection Adviser consultation where scope is in, adjacent to, above or below an imaging suite |  | See Room/Ward/Theatre Refresh checklist |

Stage 5 – Manufacturing and Construction

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Asbestos removal completed and clearance certificates issued before follow-on trades commence |  | CAR 2012 |
| Contractor method statements and permit-to-work records for roof/height access |  | Work at Height Regulations 2005 |
| PVG-checked contractor attendance records |  |  |
| Weather-protection and containment records maintained throughout construction |  |  |
| Temporary works design and sign-off (edge protection, scaffolding, weather screens) |  |  |

Stage 6 – Handover

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full commissioning records (water-tightness testing, thermal performance verification) |  | BS 6229:2025 |
| Asbestos re-inspection/clearance documentation filed in the Health & Safety File |  | CAR 2012 |
| O&M manuals, warranties and as-built drawings |  |  |
| Confirmation of Radiation Protection Adviser sign-off where applicable |  |  |

Stage 7 – Use

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Ongoing roof/envelope condition inspection regime established |  |  |
| Updated asbestos register reflecting removed/remaining materials |  | CAR 2012 Duty to Manage |
| Updated maintenance regime integrated with the wider PPM programme |  |  |

Cross-Stage / Continuous Deliverables

- Live Health & Safety File, updated with asbestos survey and removal records

- Project risk register (updated at each stage)

- Weather-protection and IPC containment plan maintained for the duration of any works over or adjacent to occupied clinical areas

- Evidence of current PVG Scheme membership for all contractor personnel attending site

- Where works are in, adjacent to, above or below a room housing ionising-radiation imaging equipment (CT, X-ray, fluoroscopy, nuclear medicine): confirm Radiation Protection Adviser (RPA) sign-off on shielding integrity per the Room/Ward/Theatre Refresh checklist - a separate gate from HAI-SCRIBE, not covered by it