Deliverables Checklist Replacement / Upgrade of Automatic Doors in a Hospital Aligned to RIBA Plan of Work 2020 & relevant Standards

This checklist follows the exact same format as the other Hard FM system checklists. It is intended for projects involving the replacement, major upgrade or installation of automatic (power-operated) doors in hospital premises (sliding, swing, revolving and folding doorsets, including fire/smoke-resisting doorsets, access-controlled doors and doors on isolation-room or theatre lobbies).

Primary Guidance References

| System Element | Key Guidance |
| --- | --- |
| Catering / Kitchen Equipment | Gas Safety (Installation and Use) Regulations 1998 (gas-fired appliances); BESA DW/172 (kitchen extract ductwork design) with BESA TR19 (grease-duct cleaning / fire-risk cadence) |
| Refrigeration & Cold Storage | F-Gas Regulations (refrigerant handling and leak-check regime); COSHH (kitchen cleaning chemicals) |
| Water-Using Equipment | Water Supply (Water Fittings) (Scotland) Byelaws 2014 / WRAS backflow prevention (warewashers, ice machines, combi-ovens); Legionella control per Domestic Hot & Cold Water Systems Replacement checklist |
| Mechanical Safety | PUWER 1998 (dishwashers, mixers, slicers, potato peelers - guarding and interlocks) |
| Supporting | Trade effluent consent and grease management - see Drainage & Foul Water System Replacement checklist (not duplicated here); Food Hygiene (Scotland) Regulations / Food Standards Scotland interface for food-service continuity |
| Core Standards | Gas Safety (Installation and Use) Regulations 1998, BESA DW/172 and TR19, F-Gas Regulations, COSHH, PUWER 1998 |

Key Principles

- Gas-fired catering appliances require Gas Safety (Installation and Use) Regulations 1998 compliance — distinct from the electrical/mechanical commissioning of the equipment itself.

- Kitchen extract ductwork is a recognised fire risk pathway (grease deposition) — design to BESA DW/172 (including its May 2024 fire/smoke-ductwork addendum) and maintain to BESA TR19's ongoing cleaning cycle, not a one-off design step.

- Warewashers, ice machines and combi-ovens connected to the mains water supply require backflow protection under the Water Supply (Water Fittings) (Scotland) Byelaws 2014 / WRAS-approved devices.

- Continuity of catering service, or an equivalent temporary catering arrangement, must be maintained during any phased replacement — a full kitchen shutdown is rarely acceptable in an operational hospital.

- Trade effluent/grease consent and drainage interface sign-off is managed via the Drainage & Foul Water Systems Replacement checklist, not duplicated here — this checklist covers the appliances and extract/refrigeration plant only.

Stage 0 – Strategic Definition

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Business case / need identification (appliance age, reliability, capacity, extract system condition) |  | PM check |
| Strategic brief & project outcomes (food-service continuity, catering operational impact) |  |  |
| High-level operational impact assessment (affected kitchen areas, food-service continuity, Food Standards Scotland interface) |  | Food Hygiene (Scotland) Regulations |
| Confirmation of which appliances are gas-fired versus electric |  | Gas Safety (Installation and Use) Regulations 1998 |

Stage 1 – Preparation and Briefing

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Project Brief (appliance schedule, gas/electric split, extract and refrigeration scope) |  |  |
| Existing condition surveys (appliances, extract canopies/ductwork, refrigeration plant) |  | BESA DW/172 |
| Extract ductwork condition and last cleaning record review |  | BESA TR19 |
| Initial risk register (food-service continuity, extract fire risk, gas safety) |  | CDM |
| Project Execution Plan & procurement strategy |  |  |
| Engagement with Catering/Facilities, Estates, Environmental Health / Food Standards Scotland and Fire Safety Advisor |  | Essential |
| Confirmation of existing trade effluent consent baseline |  | See Drainage & Foul Water checklist |

Stage 2 – Concept Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Concept design options (appliance types, extract system routing, refrigeration layout) |  | BESA DW/172 |
| Outline temporary catering strategy to maintain food service during works |  | Critical for continuity |
| Outline fire-suppression strategy for the cooking line (wet-chemical/Ansul-type extinguishing system with extract-fan and gas-supply interlock) |  | BS EN 12845 - see Fire Suppression Systems Replacement checklist |
| Design risk assessment (extract fire risk, CDM) |  |  |
| Preliminary specifications & cost plan |  |  |

Stage 3 – Spatial Coordination

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Coordinated design (extract ductwork routing and fire compartmentation per DW/172, refrigeration plant room location, gas pipework routing) |  | BESA DW/172 |
| Spatial coordination with structure, fire compartmentation and adjacent clinical/public areas |  |  |
| Updated cost plan, risk register and temporary catering continuity phasing |  |  |
| Confirmation of trade effluent/grease-management interface with the drainage works (if concurrent) |  | See Drainage & Foul Water checklist |

Stage 4 – Technical Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full technical design drawings, appliance schedules and extract ductwork design |  | BESA DW/172 |
| Gas safety design - pipework, ventilation and appliance installation compliant with statutory requirements |  | Gas Safety (Installation and Use) Regulations 1998 |
| Fire-suppression system design for the cooking line, with extract-fan and gas-supply shutdown interlock on activation |  | BS EN 12845 |
| Refrigeration design (F-Gas compliant refrigerant selection, leak-detection provision) |  | F-Gas Regulations |
| Water and backflow-prevention design for warewashers, ice machines and combi-ovens |  | WRAS |
| Electrical and control system design (extract fan interlocks, BMS integration) |  | SHTM 06 series |
| Building Regulations / statutory compliance information |  | Building (Scotland) Regulations 2004 |
| Pre-construction information & input to Construction Phase Plan |  | CDM |
| Designer's Risk Assessment & residual risks |  | CDM |
| Tender documentation / Scope of Works / pricing schedules |  |  |
| Stakeholder review and approval of design (Estates, Catering/Facilities, Fire Safety Advisor, Environmental Health) |  | Essential |
| Obtain minimum of two competitive quotations |  | Critical commercial requirement |
| Submit quotations, cost comparison and recommendation to PFI Board / NHS for lifecycle approval |  |  |
| PRE-CONTRACT HOLD POINT: No contractor appointment and no further progression until written cost approval is received |  | Clear commercial & governance cut-off |

Stage 5 – Manufacturing and Construction

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Contractor method statements, detailed phasing & temporary catering continuity arrangements |  | Critical for clinical service |
| Material & equipment certificates (appliances, fire-rated ductwork, fire-suppression components) |  | BESA DW/172 |
| Installation of appliances, extract ductwork, refrigeration plant and controls |  |  |
| Gas safety installation testing (Gas Safe registered engineer) |  | Gas Safety (Installation and Use) Regulations 1998 |
| Fire-suppression and extract/gas-interlock installation testing |  | BS EN 12845 |
| Progress records, quality inspections, change control log |  |  |
| Environmental Health / IPC sign-off for any works affecting food-preparation areas |  |  |
| Decommissioning & disposal records of redundant appliances |  |  |

Stage 6 – Handover

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full commissioning records - gas safety certification, appliance performance, extract airflow verification |  | Gas Safety (Installation and Use) Regulations 1998 |
| Fire-suppression system commissioning, including extract-fan/gas-shutoff interlock test on activation |  | BS EN 12845 |
| F-Gas commissioning and leak-detection verification records |  | F-Gas Regulations |
| Water/backflow-prevention commissioning records |  | WRAS |
| As-fitted drawings, appliance schedules and control system configuration records |  |  |
| Comprehensive O&M manuals |  |  |
| Updated Health & Safety File |  | CDM |
| Training & demonstration records for catering and estates staff |  |  |
| Practical Completion / handover certificate |  |  |
| Formal client / stakeholder acceptance |  |  |
| Confirmation of ongoing DW/172 extract-duct cleaning regime (per TR19) and annual gas-safety inspection |  | BESA TR19 |

Stage 7 – Use

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Soft landings / post-occupancy review (reliability, food-service continuity, user feedback) |  |  |
| Ongoing extract-duct cleaning regime in operation, aligned to fire risk assessment |  | BESA TR19 |
| Ongoing annual gas-safety inspection regime |  | Gas Safety (Installation and Use) Regulations 1998 |
| Ongoing F-Gas refrigerant leak-check regime |  | F-Gas Regulations |
| Defects liability records & final account |  |  |
| Lessons learned report |  |  |

Cross-Stage / Continuous Deliverables

Live Health & Safety File

Project risk register (updated at each stage)

Change control log

Stakeholder engagement (Estates, Catering/Facilities, Environmental Health / Food Standards Scotland, Fire Safety Advisor) at key gateways

Maintenance of food-service continuity throughout the works

Evidence of compliance with Gas Safety (Installation and Use) Regulations 1998, BESA DW/172 and F-Gas Regulations

Ongoing periodic extract-duct cleaning (TR19) and gas-safety inspection regime

- Evidence of current PVG Scheme membership for all contractor personnel attending site

- Where works are in, adjacent to, above or below a room housing ionising-radiation imaging equipment (CT, X-ray, fluoroscopy, nuclear medicine): confirm Radiation Protection Adviser (RPA) sign-off on shielding integrity per the Room/Ward/Theatre Refresh checklist - a separate gate from HAI-SCRIBE, not covered by it