Deliverables Checklist Replacement / Upgrade of Escalators in a Hospital Aligned to RIBA Plan of Work 2020 & relevant Standards

This checklist follows the exact same format as the other Hard FM system checklists. It is intended for projects involving the installation, replacement or major upgrade of escalators and moving walks in hospital premises. Escalators are a distinct system from passenger, bed and firefighting/escape lifts - see Lift & Vertical Transportation Replacement for those. This is a lower-volume, site-conditional checklist: only relevant where a site actually has, or is adding, escalators or moving walks.

Primary Guidance References

| System Element | Key Guidance |
| --- | --- |
| Design & construction | BS EN 115-1:2017 (Safety of escalators and moving walks - Construction and installation, superseding BS EN 115-1:2008+A1:2010) sets the design and construction safety requirements for new escalators and moving walks. |
| Existing installations | BS EN 115-2 sets rules for the improvement of safety of existing escalators and moving walks, relevant to major upgrade rather than new-installation projects. |
| Statutory inspection regime | LOLER 1998 does NOT apply to escalators or moving walks - HSE guidance confirms this exclusion applies because their principal function is to transport people, not to lift loads. PUWER 1998 applies instead, alongside regulation 19 of the Workplace (Health, Safety and Welfare) Regulations 1992, for maintenance and inspection duties. |
| Site relevance | Confirm at Stage 0 whether the site actually has, or is proposing to add, escalators - this checklist should not be applied by default to every capital project the way Electrical Services or Fire Alarm checklists are. |

Key Principles

- This checklist only applies where a site genuinely has, or is adding, escalators or moving walks - confirm site relevance at Stage 0 rather than defaulting it into every capital-project scope.

- LOLER 1998 does not apply to escalators (confirmed via HSE guidance: their principal function is to transport, not lift) - do not apply a LOLER thorough-examination regime by analogy with lifts; PUWER 1998 governs maintenance and inspection instead.

- A major upgrade of an existing escalator should be assessed against BS EN 115-2 (improvement of safety of existing installations), not solely BS EN 115-1, which is written for new construction.

- Continuity of horizontal/vertical circulation for patients, staff and visitors must be planned for the works duration - an escalator taken out of service in a high-footfall area is a real operational impact, not a minor inconvenience.

Stage 0 – Strategic Definition

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Business case / need identification (escalator age, reliability, capacity, footfall analysis) |  | BS EN 115-1:2017 |
| Confirmation that the site has, or requires, escalator provision (site-relevance check) |  |  |
| Expanded risk register |  | SHTM 00, CDM 2015 |

Stage 1 – Preparation and Briefing

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Project Brief (scope: new installation vs major upgrade of existing unit) |  |  |
| Existing escalator condition survey (drive system, steps, balustrades, safety devices) |  | BS EN 115-2 |
| Baseline footfall / usage data and residual life assessment |  |  |

Stage 2 – Concept Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Concept design options (full replacement vs modernisation, capacity, rise/pitch) |  | BS EN 115-1:2017 |
| Outline circulation strategy for the works period (alternative routes, temporary lift capacity) |  |  |

Stage 3 – Spatial Coordination

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Coordinated design (structural opening, balustrade/handrail interfaces, fire-compartmentation interfaces) |  |  |
| Confirmed structural loading and pit/headroom dimensions |  |  |

Stage 4 – Technical Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full technical design drawings and specifications |  | BS EN 115-1:2017 |
| Fire and smoke-compartmentation strategy for the escalator void |  |  |
| PUWER-compliant maintenance and inspection regime specified |  | PUWER 1998 |

Stage 5 – Manufacturing and Construction

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Installation records and contractor method statements |  |  |
| PVG-checked contractor attendance records |  |  |
| Temporary circulation/signage arrangements maintained throughout works |  |  |

Stage 6 – Handover

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full commissioning records and safety-device functional tests |  | BS EN 115-1:2017 |
| O&M manuals, warranties and as-built drawings |  |  |
| Confirmation of PUWER inspection regime handed to the maintenance provider |  | PUWER 1998 |

Stage 7 – Use

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Ongoing PUWER-compliant maintenance and statutory inspection regime |  | PUWER 1998, Workplace Regs reg 19 |
| Updated maintenance regime integrated with the wider PPM programme |  |  |

Cross-Stage / Continuous Deliverables

- Live Health & Safety File

- Project risk register (updated at each stage)

- Confirmation that no LOLER thorough-examination regime has been mistakenly applied to the escalator in place of the correct PUWER regime

- Evidence of current PVG Scheme membership for all contractor personnel attending site

- Where works are in, adjacent to, above or below a room housing ionising-radiation imaging equipment (CT, X-ray, fluoroscopy, nuclear medicine): confirm Radiation Protection Adviser (RPA) sign-off on shielding integrity per the Room/Ward/Theatre Refresh checklist - a separate gate from HAI-SCRIBE, not covered by it