Deliverables Checklist Replacement / Upgrade of Automatic Doors in a Hospital Aligned to RIBA Plan of Work 2020 & relevant Standards

This checklist follows the exact same format as the other Hard FM system checklists. It is intended for projects involving the replacement, major upgrade or installation of automatic (power-operated) doors in hospital premises (sliding, swing, revolving and folding doorsets, including fire/smoke-resisting doorsets, access-controlled doors and doors on isolation-room or theatre lobbies).

Primary Guidance References

| System Element | Key Guidance |
| --- | --- |
| Facility Design | SHPN 16-01 Mortuary and post mortem facilities: design and briefing guidance, v2.0 Nov 2017 - Scotland's current design guidance, superseding the withdrawn HBN 20 (NHS England's current equivalent is HBN 16-01, 2023) |
| Ventilation | PM Room designed with supply/extract balanced to maintain negative pressure, -5 Pa to -15 Pa, 100% fresh air (SHPN 16-01 section 6.72); cross-references SHTM 03-01 |
| Refrigeration | Body-storage refrigeration plant - F-Gas Regulations (refrigerant handling); continuous temperature-monitoring and alarm requirement |
| Legal Framework | Human Tissue (Scotland) Act 2006 governs the clinical/legal process - named here for context only; this checklist covers the engineering/estates deliverables, not clinical or legal procedure |
| Supporting | HAI-SCRIBE (infection control interface); CDM 2015 |
| Core Standards | SHPN 16-01, SHTM 03-01, F-Gas Regulations, Human Tissue (Scotland) Act 2006 |

Key Principles

- Scotland's current primary source for mortuary facility design is SHPN 16-01 v2.0 (Nov 2017) — HBN 20 (the older England-derived reference) is withdrawn.

- Post-mortem room ventilation must maintain negative pressure of -5 Pa to -15 Pa with 100% fresh air (SHPN 16-01 §6.72), cross-referencing SHTM 03-01 — a genuine ventilation-design deliverable, not a generic HVAC assumption.

- Mortuary refrigeration plant using F-Gas refrigerants falls under the F-Gas Regulations — leak-check and register requirements are distinct statutory steps from general commissioning.

- Infection prevention and control for mortuary/post-mortem areas is managed via HAI-SCRIBE (SHFN 30) — apply the same multidisciplinary risk-assessment process used elsewhere in this project's clinical-adjacent checklists.

- The Human Tissue (Scotland) Act 2006 is the governing legal framework for mortuary/post-mortem operations — this checklist covers the engineering/estates deliverables only, not clinical or legal process content, which sits outside Hard FM's scope.

Stage 0 – Strategic Definition

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Business case / need identification (mortuary/refrigeration condition, reliability, capacity) |  | SHPN 16-01 |
| Strategic brief & project outcomes (dignity of service, operational continuity) |  |  |
| High-level infection control impact assessment |  | HAI-SCRIBE |
| Confirmation of scope - body store, PM suite, viewing, teaching/research areas per SHPN 16-01's modular functional elements |  | SHPN 16-01 |

Stage 1 – Preparation and Briefing

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Project Brief (scope per SHPN 16-01 functional modules) |  | SHPN 16-01 |
| Existing condition surveys (refrigeration plant, ventilation, PM suite fittings) |  |  |
| Initial risk register (body-storage continuity, infection control, refrigeration failure) |  | CDM |
| Engagement with Estates, IPC, Pathology/Bereavement Services and Fire Safety Advisor |  | Essential |
| Project Execution Plan & procurement strategy |  |  |

Stage 2 – Concept Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Concept design options (refrigeration capacity and resilience/redundancy strategy) |  | SHPN 16-01 |
| Outline ventilation strategy for the PM Room, targeting negative pressure per SHPN 16-01 |  | SHPN 16-01, SHTM 03-01 |
| Design risk assessment (CDM, HAI-SCRIBE) |  |  |
| Preliminary specifications & cost plan |  |  |

Stage 3 – Spatial Coordination

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Coordinated design (refrigeration plant room location, PM Room ventilation ductwork routing and pressure-cascade coordination) |  | SHTM 03-01 |
| Spatial coordination with structure and adjacent clinical/public areas, including dignity and privacy considerations |  |  |
| Updated cost plan and risk register |  |  |
| Temporary body-storage continuity strategy during works |  | Critical - zero tolerance for loss of refrigeration |

Stage 4 – Technical Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full technical design - refrigeration system design, F-Gas compliant refrigerant, resilience/redundancy |  | F-Gas Regulations |
| PM Room ventilation design confirming negative pressure of -5 Pa to -15 Pa and 100% fresh air |  | SHPN 16-01 section 6.72 |
| Temperature-monitoring and alarm system design, with critical alarm routed to the BMS |  |  |
| Building Regulations / statutory compliance information |  | Building (Scotland) Regulations 2004 |
| Pre-construction information & input to Construction Phase Plan |  | CDM |
| Designer's Risk Assessment & residual risks |  | CDM |
| Tender documentation / Scope of Works / pricing schedules |  |  |
| Stakeholder review and approval of design (Estates, IPC, Pathology/Bereavement Services, Fire Safety Advisor) |  | Essential |
| Obtain minimum of two competitive quotations |  | Critical commercial requirement |
| Submit quotations, cost comparison and recommendation to PFI Board / NHS for lifecycle approval |  |  |
| PRE-CONTRACT HOLD POINT: No contractor appointment and no further progression until written cost approval is received |  | Clear commercial & governance cut-off |

Stage 5 – Manufacturing and Construction

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Contractor method statements, phasing & temporary body-storage continuity arrangements |  | Critical - zero tolerance |
| Material & equipment certificates (refrigeration plant, ventilation) |  |  |
| Installation of refrigeration plant, ventilation ductwork and controls |  |  |
| Commissioning of temperature-monitoring and alarm interlocks |  |  |
| Progress records, quality inspections, change control log |  |  |
| IPC sign-off |  | HAI-SCRIBE |
| Decommissioning & disposal records of redundant plant |  |  |

Stage 6 – Handover

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full commissioning & validation records - refrigeration temperature performance |  |  |
| PM Room negative-pressure verification against the -5 Pa to -15 Pa range |  | SHPN 16-01 section 6.72 |
| Temperature-monitoring and alarm system testing, including BMS integration |  |  |
| As-fitted drawings and control system configuration records |  |  |
| Comprehensive O&M manuals |  |  |
| Updated Health & Safety File |  | CDM |
| Training & demonstration records for Estates and Pathology/Bereavement Services staff |  |  |
| Practical Completion / handover certificate |  |  |
| Confirmation of ongoing periodic negative-pressure and refrigeration verification regime |  | SHTM 03-01 |

Stage 7 – Use

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Soft landings / post-occupancy review (reliability, body-storage continuity, user feedback) |  |  |
| Ongoing periodic negative-pressure verification regime in operation, aligned to the SHTM 03-01 ventilation verification cycle |  | SHTM 03-01 |
| Ongoing refrigeration temperature-monitoring and alarm regime |  |  |
| Ongoing F-Gas refrigerant leak-check regime |  | F-Gas Regulations |
| Defects liability records & final account |  |  |
| Lessons learned report |  |  |

Cross-Stage / Continuous Deliverables

Live Health & Safety File

Project risk register (updated at each stage)

Change control log

Stakeholder engagement (Estates, IPC, Pathology/Bereavement Services, Fire Safety Advisor) at key gateways

Maintenance of body-storage continuity throughout the works - zero tolerance for loss of refrigeration

Evidence of compliance with SHPN 16-01 and SHTM 03-01

Ongoing periodic negative-pressure and refrigeration-monitoring verification regime

- Evidence of current PVG Scheme membership for all contractor personnel attending site

- Where works are in, adjacent to, above or below a room housing ionising-radiation imaging equipment (CT, X-ray, fluoroscopy, nuclear medicine): confirm Radiation Protection Adviser (RPA) sign-off on shielding integrity per the Room/Ward/Theatre Refresh checklist - a separate gate from HAI-SCRIBE, not covered by it