Deliverables Checklist Installation / Upgrade of Renewable & Net Zero Plant in a Hospital Aligned to RIBA Plan of Work 2020 & relevant Standards

This checklist follows the exact same format as the other Hard FM system checklists. It is intended for projects involving the installation, replacement or major upgrade of renewable and net zero energy plant in hospital premises (roof/ground-mounted solar PV, air/ground source heat pumps, battery energy storage systems (BESS), and EV charging infrastructure).

Primary Guidance References

| System Element | Key Guidance |
| --- | --- |
| Solar PV | MCS MIS 3002 (Solar PV Installation Standard, current edition) governs design and installation; grid connection via ENA Engineering Recommendation G98 (notify-after-install, up to 16A/phase) or G99 (approve-before-install, larger schemes) - G98/G99 replaced the older G83/G59 regimes in 2019. |
| Heat Pumps (ASHP/GSHP) | MCS MIS 3005-D (Design) and MIS 3005-I (Installation) - the former combined MIS 3005 standard split into separate design/installation standards, mandatory for MCS contractors since 01/04/2022. Only systems up to 45kWth may be MCS-certified. |
| Battery Energy Storage (BESS) | NFCC Grid Scale Battery Energy Storage System Planning guidance for fire and rescue services sets fire-safety and siting expectations (indicative minimum 25m separation from occupied buildings prior to any mitigation); a DSEAR risk assessment is required for the flammable off-gas/thermal-runaway hazard from lithium-ion cells, per HSE guidance - this is in addition to, not instead of, electrical safety compliance. |
| EV Charging Infrastructure | BS EN IEC 61851 (electric vehicle conductive charging system) and the IET Code of Practice for Electric Vehicle Charging Equipment Installation govern design and installation, including protective device selection and PME earthing considerations for open-access car parks. |

Key Principles

- A DNO grid-connection application (G98 for small-scale, G99 approve-before-install for larger schemes) must be submitted before any design is finalised - G99 approval timescales can materially affect programme and must be tracked as a critical-path item, not a late-stage formality.

- A BESS DSEAR risk assessment and fire strategy (informed by NFCC guidance) must be completed before siting is fixed - proximity to occupied wards, escape routes, fresh-air intakes and combustible materials is a real siting constraint, not a detail to resolve after layout is agreed.

- Any heat pump or solar retrofit must be checked against existing SHTM 03-01 ventilation/thermal-comfort requirements before design is committed - decarbonisation measures must not compromise clinical ventilation performance; see the separate energy/net-zero compliance assessment for the energy-gainshare and ventilation-conflict angle this checklist does not itself cover.

- Net zero deliverables should be tracked against the health board's own NHS Scotland Climate Emergency and Sustainability Strategy: 2022-2026 carbon-reduction trajectory (net zero estate emissions targeted by 2040, 70% reduction by 2030, supply-chain net zero by 2045), not treated as a standalone environmental add-on disconnected from the wider estate strategy.

- Continuity of clinical electrical resilience must be maintained throughout any works interfacing with the existing standby power/UPS system - see Electrical Services Replacement for generator/UPS/switchgear interface deliverables; this checklist does not duplicate that scope.

Stage 0 – Strategic Definition

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Business case / need identification (existing energy performance baseline, carbon-reduction target, plant condition) |  | NHS Scotland Climate Emergency and Sustainability Strategy: 2022-2026 |
| Initial stakeholder map, including Estates, Energy Manager and Finance |  |  |
| Preliminary roof-loading / land-availability feasibility check (solar PV, ASHP siting) |  |  |
| Preliminary DNO capacity enquiry (headroom check ahead of a full G98/G99 application) |  | ENA G98/G99 |
| Expanded risk register |  | SHTM 00, CDM 2015 |

Stage 1 – Preparation and Briefing

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Project Brief (scope: PV capacity, heat pump type/capacity, BESS capacity, EV charging point count) |  |  |
| Existing system condition surveys (roof condition, existing boiler/plant interface, electrical infrastructure capacity) |  |  |
| Formal DNO pre-application enquiry submitted |  | ENA G98/G99 |
| Site-specific fire risk and DSEAR scoping for any proposed BESS |  | DSEAR, NFCC guidance |
| Engagement with Fire Safety Advisor and Energy Manager |  |  |
| Sustainability/net zero benefits case aligned to the NHS Scotland Climate Emergency and Sustainability Strategy: 2022-2026 |  |  |

Stage 2 – Concept Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Concept design options (PV array layout/orientation, heat pump type ASHP vs GSHP, BESS chemistry and capacity) |  | MIS 3002, MIS 3005-D |
| Outline grid-connection strategy and indicative G98/G99 route |  | ENA G98/G99 |
| Outline BESS siting and separation-distance assessment |  | NFCC guidance |
| Structural feasibility for roof-mounted PV / heat pump plant loading |  |  |

Stage 3 – Spatial Coordination

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Coordinated design (PV array layout, heat pump plant room/external unit location, BESS enclosure location, EV charge-point bay layout) |  |  |
| Confirmed structural loading assessment (roof, plant room, ground-bearing for BESS enclosures) |  |  |
| Interfaces with existing electrical distribution, BMS and heating systems mapped |  |  |
| Updated risk register |  |  |

Stage 4 – Technical Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full technical design drawings and specifications |  | MIS 3002, MIS 3005-D/I |
| DSEAR risk assessment finalised for BESS (thermal-runaway detection, ventilation, separation distances) |  | DSEAR, NFCC guidance |
| Fire strategy addendum covering BESS and any new plant rooms |  |  |
| Formal G98/G99 connection application submitted and connection offer received |  | ENA G98/G99 |
| MCS-certified installer/contractor confirmed for PV and heat pump scopes |  | MIS 3002, MIS 3005-I |
| EV charging circuit design (protective device selection, PME earthing assessment for open-access areas) |  | BS EN IEC 61851, IET CoP |
| Verification that heat pump/PV retrofit does not compromise SHTM 03-01 ventilation or thermal-comfort requirements |  | SHTM 03-01 |

Stage 5 – Manufacturing and Construction

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Installation carried out per MCS standards, with progress records |  | MIS 3002, MIS 3005-I |
| Contractor method statements and permit-to-work records for any live electrical isolations |  |  |
| PVG-checked contractor attendance records |  |  |
| BESS installation verified against DSEAR risk assessment and fire strategy |  |  |
| G98/G99 notification or pre-energisation approval obtained from the DNO before energisation |  | ENA G98/G99 |

Stage 6 – Handover

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full commissioning records (PV yield test, heat pump performance verification, BESS functional/fire-detection test, EV charge-point functional test) |  | MIS 3002, MIS 3005-I |
| MCS certification issued for PV and heat pump installations |  | MIS 3002, MIS 3005-I |
| DNO connection agreement finalised (G98 notification accepted / G99 approval confirmed) |  | ENA G98/G99 |
| O&M manuals, warranties and as-built drawings |  |  |
| Operator training on BMS integration and BESS emergency shutdown procedures |  |  |

Stage 7 – Use

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Ongoing performance monitoring against MCS commissioning benchmarks (PV yield, heat pump COP) |  |  |
| BESS fire-detection and DSEAR risk assessment review on a defined periodic cycle |  | DSEAR |
| Updated maintenance regime integrated with the BMS and wider PPM programme |  |  |
| Annual carbon/energy performance reported against the NHS Scotland Climate Emergency and Sustainability Strategy: 2022-2026 trajectory |  |  |

Cross-Stage / Continuous Deliverables

- Ongoing DNO G98/G99 connection agreement compliance (export limits, protection settings) maintained throughout system life

- BESS DSEAR risk assessment and fire strategy reviewed on a defined periodic cycle, not treated as a one-off Stage 4 exercise

- MCS certification and commissioning records retained for the life of the installation

- Evidence of current PVG Scheme membership for all contractor personnel attending site

- Where works are in, adjacent to, above or below a room housing ionising-radiation imaging equipment (CT, X-ray, fluoroscopy, nuclear medicine): confirm Radiation Protection Adviser (RPA) sign-off on shielding integrity per the Room/Ward/Theatre Refresh checklist - a separate gate from HAI-SCRIBE, not covered by it