Deliverables Checklist Ward / Theatre / Clinical Area Refurbishment (including Mental Health Ligature Improvements) Aligned to RIBA Plan of Work 2020, HAI-SCRIBE & relevant Standards

This checklist follows the exact same format as the previous 17 Hard FM system checklists. It is intended for projects involving the refurbishment or refresh of wards, theatres and clinical areas, including:

- Safe ligature improvements (windows, doors, ensuite doors) in Mental Health Units (MHU)

- Standard room refreshes (flooring, wall cladding such as Altro, decoration, joinery)

- Theatre refreshes (finishes, minor M&E interfaces, validation)

Primary Guidance References

| Element | Key Guidance |
| --- | --- |
| Overarching | SHTM 00 – Policies and principles HAI-SCRIBE (SHFN 30) |
| Mental Health / Ligature | Design guidance for Mental Health environments Anti-ligature product standards and clinical risk assessment |
| Clinical Areas & Finishes | Infection Prevention & Control requirements Relevant HTM/SHTM guidance on clinical environments |
| Interfaces | SHTM 03-01 (Ventilation – especially theatres) SHTM 02-01 (Medical Gas terminal units) SHTM 08-03 (Nurse Call) SHTM 04-01 / Building Standards (Drainage & water) SHTM 06 series (Electrical) |
| Core Standards | Building Standards (Scotland) CDM 2015 Relevant British Standards for finishes, doors, windows and ironmongery |

Key Principles

- Patient and staff safety (especially ligature risk in Mental Health) is paramount.

- HAI-SCRIBE must be applied rigorously (High involvement expected).

- Where the refurbishment is in, adjacent to, above or below an imaging/radiation room, RPA sign-off on shielding integrity is a separate required gate alongside HAI-SCRIBE, not covered by it.

- Continuity of clinical service and infection control during the works is critical.

- Interfaces with existing engineering systems (ventilation, medical gases, electrical, nurse call, drainage) must be carefully managed.

- Cleanability, durability and maintenance access of new finishes are essential.

Stage 0 – Strategic Definition

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Business case / need identification (condition, ligature risk, clinical functionality, infection risk) |  | SHTM 00, HAI-SCRIBE Stage 1 |
| Strategic brief & project outcomes (patient safety, clinical environment, infection control, ligature reduction) |  | SHTM 00 |
| High-level clinical / operational impact assessment |  | Clinical + IPC |

Stage 1 – Preparation and Briefing

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Project Brief (scope: ligature works, finishes, theatres, rooms affected) |  | SHTM 00, HAI-SCRIBE Stage 1 |
| Existing condition surveys (fabric, doors, windows, ensuites, finishes, known risks) |  | — |
| Ligature risk assessment (MHU areas) |  | Mental Health guidance |
| Initial risk register (ligature, infection, clinical disruption, fire, asbestos) |  | CDM, HAI-SCRIBE, IPC |
| Project Execution Plan & procurement strategy |  | — |
| Early engagement with Clinical, IPC, Mental Health, Estates and Soft FM teams |  | Essential |

Stage 2 – Concept Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Concept design options (ligature solutions, finishes strategy, phasing, decant requirements) |  | HAI-SCRIBE Stage 2 |
| Outline clinical environment strategy (infection control, cleanability, durability) |  | IPC |
| Preliminary room data sheets / layouts |  | — |
| Outline specifications & preliminary cost plan |  | — |
| Design risk assessment (including ligature and HAI risks) |  | CDM, HAI-SCRIBE |

Stage 3 – Spatial Coordination

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Coordinated design (doors, windows, ensuite layouts, finishes interfaces with services) |  | HAI-SCRIBE Stage 2 |
| Spatial coordination with existing M&E services, fire strategy and clinical flows |  | SHTM 00 |
| Updated cost plan, risk register & detailed phasing / decant strategy |  | — |
| Confirmation of temporary clinical arrangements |  | Clinical stakeholders |

Stage 4 – Technical Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full technical design drawings, room layouts, door/window schedules, finishes schedules |  | — |
| Detailed specifications (anti-ligature products, flooring, wall cladding, ironmongery, ceilings) |  | Relevant BS / manufacturer |
| Interface design with ventilation, medical gases, electrical, nurse call, drainage and fire systems |  | Relevant SHTMs |
| HAI-SCRIBE Stage 2 design review and infection control measures |  | HAI-SCRIBE Stage 2 |
| Fire strategy and means of escape implications |  | Firecode |
| Building Standards / statutory compliance information |  | Building Standards (Scotland) |
| Asbestos refurbishment & demolition (R&D) survey obtained and reviewed prior to any fabric-disturbing works |  | CAR 2012 (Control of Asbestos Regulations 2012), Regulation 5 |
| Pre-construction information & input to Construction Phase Plan |  | CDM |
| Designer’s Risk Assessment & residual risks |  | CDM, HAI-SCRIBE |
| Tender documentation / Scope of Works / pricing schedules |  | — |
| Clinical, IPC and Mental Health stakeholder review and approval of design |  | Essential |
| Radiation Protection Adviser (RPA) sign-off confirming shielding integrity unaffected (where scope is in, adjacent to, above or below a room housing ionising-radiation imaging equipment - CT, X-ray, fluoroscopy, nuclear medicine; not MRI, which uses no ionising radiation) |  | IRR17 - separate gate from HAI-SCRIBE, not a substitute for it |

Stage 5 – Manufacturing and Construction

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Contractor method statements, detailed phasing, decant and temporary clinical arrangements |  | Critical |
| Material & product certificates (anti-ligature items, flooring, cladding, doors, windows) |  | Manufacturer |
| Installation of doors, windows, ironmongery, flooring, wall cladding and associated works |  | — |
| Protection of existing services and clinical areas |  | HAI-SCRIBE Stage 3 |
| Dust, water and infection control measures during construction |  | HAI-SCRIBE Stage 3 |
| Progress records, quality inspections, change control log |  | — |
| Temporary arrangements and clinical continuity records |  | Essential |
| Decommissioning / strip-out records of redundant finishes and fittings |  | — |

Stage 6 – Handover

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full inspection, snagging and quality verification records |  | — |
| Ligature safety verification and clinical sign-off (MHU areas) |  | Mental Health / Clinical |
| Cleaning, terminal clean and IPC clearance |  | HAI-SCRIBE Stage 4, IPC |
| As-fitted drawings, schedules and product information |  | — |
| Comprehensive O&M manuals and maintenance information for new finishes and fittings |  | SHTM 00 |
| Updated Health & Safety File |  | CDM |
| Training & demonstration records for clinical, Soft FM and Estates staff |  | — |
| Residual risk register |  | CDM |
| Practical Completion / handover certificate |  | — |
| Formal clinical, IPC and client acceptance |  | Essential |
| HAI-SCRIBE Stage 4 pre-handover check completion |  | HAI-SCRIBE Stage 4 |

Stage 7 – Use

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Soft landings / post-occupancy review (clinical functionality, ligature safety, cleanability, user feedback) |  | SHTM 00, HAI-SCRIBE Stage 4 |
| Updated operational and cleaning procedures |  | IPC / Soft FM |
| Ongoing maintenance and inspection regime for anti-ligature items and finishes |  | — |
| Defects liability records & final account |  | — |
| Lessons learned report |  | SHTM 00 |

Cross-Stage / Continuous Deliverables

- Live Health & Safety File

- Project risk register (updated at each stage)

- Change control log

- HAI-SCRIBE process applied at all four stages (High involvement)

- Continuous clinical and IPC stakeholder engagement

- Maintenance of safe clinical environment and service continuity throughout the works

- Evidence of compliance with anti-ligature guidance, infection control requirements and Building Standards

- Interface management with existing engineering systems (ventilation, medical gases, electrical, nurse call, drainage, etc.)

- Evidence of current PVG Scheme membership for all contractor personnel attending site