Deliverables Checklist Installation / Upgrade of Non-Domestic Water Treatment Plant in a Hospital Aligned to RIBA Plan of Work 2020 & relevant Standards

This checklist follows the exact same format as the other Hard FM system checklists. It is intended for projects involving the installation, replacement or major upgrade of non-domestic water treatment plant serving pharmacy compounding, decontamination/CSSD, and dialysis/renal services (reverse osmosis and deionised water treatment systems and their distribution loops) - distinct from general potable water storage and distribution, see Domestic Hot & Cold Water Systems Replacement for that.

Primary Guidance References

| System Element | Key Guidance |
| --- | --- |
| Dialysis/renal water treatment | ISO 23500 series (Preparation and quality management of fluids for haemodialysis and related therapies) - Part 1 general requirements, Part 2 water treatment equipment (current edition ANSI/AAMI/ISO 23500-2:2024), Part 3 water quality requirements. |
| Pharmacy compounding water | European Pharmacopoeia Purified Water and Water for Injections monographs apply where the plant supplies pharmacy compounding - confirm applicability with Pharmacy before scoping; not every hospital site has a compounding requirement. |
| Overarching water safety | HTM 04-01 (Safe water in healthcare premises) is the overarching UK health-sector water-safety framework governing design, commissioning and ongoing management of any water system, including treatment plant. |
| Legionella control | ACOP L8 and HSG274 govern Legionella risk control for any stored or held water within the treatment process, including RO reject/break tanks. |
| Backflow prevention | WRAS-approved backflow prevention is required at the treatment plant's mains connection point, per the Water Supply (Water Fittings) (Scotland) Byelaws 2014 (administered by Scottish Water). |

Key Principles

- Confirm which end-use(s) the plant actually serves (dialysis, pharmacy compounding, CSSD/decontamination feed) at Stage 0 - the applicable water-quality standard differs by end use, and a single plant may need to meet more than one standard simultaneously if it serves multiple departments.

- ISO 23500's water-quality requirements for haemodialysis are non-negotiable clinical safety limits, not general engineering targets - commissioning water-quality testing must demonstrate compliance before the plant is handed over for clinical use, not assumed from design calculations.

- Any stored or held water within the treatment train (break tanks, RO reject storage) is a Legionella risk that must be assessed under ACOP L8/HSG274 - a treatment plant is not exempt from Legionella control just because its output is highly purified.

- This checklist covers the treatment plant and its distribution loop only - the ISO 23500 dialysis water-quality deliverable already present in Domestic Hot & Cold Water Systems Replacement covers the point-of-use dialysis station itself; avoid duplicating that deliverable, cross-reference it instead.

Stage 0 – Strategic Definition

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Business case / need identification (existing treatment plant condition, water-quality failure history, capacity) |  | HTM 04-01 |
| Confirmation of which end use(s) the plant serves (dialysis, pharmacy compounding, CSSD) |  |  |
| Expanded risk register |  | SHTM 00, CDM 2015 |

Stage 1 – Preparation and Briefing

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Project Brief (scope: RO/DI plant capacity, end uses served, distribution loop extent) |  |  |
| Existing plant condition survey and water-quality testing baseline |  | ISO 23500 |
| Engagement with Pharmacy, Renal/Dialysis and Decontamination services |  |  |

Stage 2 – Concept Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Concept design options (RO vs RO+DI, single-pass vs double-pass, loop vs point-of-use) |  | ISO 23500-2 |
| Outline Legionella control strategy for any stored/held water in the treatment train |  | ACOP L8, HSG274 |

Stage 3 – Spatial Coordination

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Coordinated design (plant room location, distribution loop routing, interfaces with dialysis stations and pharmacy compounding suite) |  |  |
| Confirmed backflow prevention arrangement at the mains connection |  | WRAS |

Stage 4 – Technical Design

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full technical design drawings and specifications |  | ISO 23500-1/2, HTM 04-01 |
| Water-quality validation plan defining acceptance criteria before clinical use |  | ISO 23500-3 |
| Legionella control measures finalised for break tanks/reject storage |  | ACOP L8, HSG274 |
| Pharmacy compounding water-quality requirements confirmed where applicable |  | European Pharmacopoeia |

Stage 5 – Manufacturing and Construction

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Installation records and contractor method statements |  |  |
| PVG-checked contractor attendance records |  |  |
| Backflow prevention device installed and WRAS-approved |  | WRAS |

Stage 6 – Handover

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Full commissioning records including water-quality validation against ISO 23500 acceptance criteria before any clinical use |  | ISO 23500-3 |
| Legionella commissioning/flushing records |  | ACOP L8, HSG274 |
| O&M manuals, warranties and as-built drawings |  |  |

Stage 7 – Use

| Deliverable | Status / Evidence | Relevant Notes |
| --- | --- | --- |
| Ongoing water-quality monitoring regime (chemical, microbiological, endotoxin as applicable) |  | ISO 23500-3 |
| Ongoing Legionella monitoring regime for stored/held water |  | ACOP L8, HSG274 |
| Updated maintenance regime integrated with the wider PPM programme |  |  |

Cross-Stage / Continuous Deliverables

- Live Health & Safety File

- Project risk register (updated at each stage)

- Cross-reference to the dialysis water-quality deliverable in Domestic Hot & Cold Water Systems Replacement, to avoid duplicated scope at the point-of-use station

- Evidence of current PVG Scheme membership for all contractor personnel attending site

- Where works are in, adjacent to, above or below a room housing ionising-radiation imaging equipment (CT, X-ray, fluoroscopy, nuclear medicine): confirm Radiation Protection Adviser (RPA) sign-off on shielding integrity per the Room/Ward/Theatre Refresh checklist - a separate gate from HAI-SCRIBE, not covered by it