Deliverables Checklist Replacement of Medical Gas Systems (including Pendants) in a Hospital Aligned to RIBA Plan of Work 2020 & relevant SHTMs

This checklist follows the same format as the previous heating/ventilation and valve/boiler checklists. It is intended for projects involving the replacement or major modification of Medical Gas Pipeline Systems (MGPS), including ceiling pendants / medical supply units, terminal units, distribution pipework, plant (manifold, VIE, compressors, vacuum plant), alarm systems and anaesthetic gas scavenging systems (AGSS).

Primary SHTM / guidance references

| System Element | Key Guidance |
| --- | --- |
| Medical Gas Pipeline Systems | SHTM 02-01 Part A – Design, installation, validation and verification SHTM 02-01 Part B – Operational management |
| Overarching / Electrical | SHTM 00 (Policies and principles) SHTM 06-01 (Electrical services – relevant for pendant power, controls and data) |
| Supporting | Medical Gas Safety Group (MGSG) requirements Permit-to-Work system Authorised Person (MGPS) / Competent Person roles BS EN ISO 7396-1, BS EN ISO 9170, BS EN ISO 11197 (medical supply units / pendants) CDM 2015 |

Key principles

- Patient safety is paramount (identity, continuity, quality and quantity of supply).

- All works must be controlled via the Permit-to-Work system and overseen by the Authorised Person (MGPS).

- Continuity of medical gas supply to clinical areas must be maintained (temporary supplies or phased isolation).

- Pendants are treated as medical supply units and must comply with relevant sections of SHTM 02-01 and BS EN ISO 11197.

Stage 0 – Strategic Definition

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Business case / need identification (system age, compliance, clinical risk, pendant condition) |  | SHTM 00, SHTM 02-01 |
| Strategic brief & project outcomes (continuity of supply, patient safety, resilience) |  | SHTM 00 |
| High-level clinical / operational impact assessment |  | SHTM 00, MGSG |

Stage 1 – Preparation and Briefing

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Project Brief (scope of MGPS / pendant replacement, continuity requirements) |  | SHTM 00, SHTM 02-01 |
| Existing system condition surveys (pipework, terminal units, pendants, plant, alarms) |  | SHTM 02-01 Part B |
| Baseline identity, quality and flow testing records |  | SHTM 02-01 Part A |
| Initial risk register (isolation risks, cross-connection, pendant structural loads) |  | SHTM 00, CDM, MGSG |
| Project Execution Plan & procurement strategy |  | — |
| Engagement with Medical Gas Safety Group (MGSG) |  | SHTM 02-01 |

Stage 2 – Concept Design

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Concept design options (phased replacement, temporary gas supplies, pendant strategy) |  | SHTM 02-01 Part A |
| Outline MGPS strategy (sources of supply, distribution, terminal units, pendants, AGSS) |  | SHTM 02-01 Part A |
| Preliminary pendant / medical supply unit selection and locations |  | SHTM 02-01, BS EN ISO 11197 |
| Outline specifications & preliminary cost plan |  | — |
| Design risk assessment |  | CDM, SHTM 00, SHTM 02-01 |

Stage 3 – Spatial Coordination

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Coordinated design (pipe routes, plant locations, pendant positions, structural supports) |  | SHTM 02-01 Part A |
| Spatial coordination with structure, electrical, data, lighting and other services |  | SHTM 06-01 |
| Updated cost plan, risk register & high-level phasing / isolation strategy |  | — |
| Confirmation of temporary supply arrangements |  | SHTM 02-01 |

Stage 4 – Technical Design

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Full technical design drawings & schematics (including phasing and isolation points) |  | SHTM 02-01 Part A |
| Detailed specifications: |  |  |
| – Pipeline systems, valves, AVSUs |  |  |
| – Terminal units |  |  |
| – Ceiling pendants / medical supply units (rigid, telescopic or articulated) |  |  |
| – Plant, manifolds, alarms, AGSS |  | SHTM 02-01 Part A, BS EN ISO 7396-1, BS EN ISO 11197 |
| Structural design information for pendant supports / ceiling fixings |  | — |
| Electrical & data design associated with pendants |  | SHTM 06-01 |
| Alarm system design and interface requirements |  | SHTM 02-01 Part A |
| Building Regulations / statutory compliance information |  | — |
| Pre-construction information & input to Construction Phase Plan |  | CDM |
| Designer’s Risk Assessment & residual risks |  | CDM, SHTM 02-01 |
| Tender documentation / Scope of Works / pricing schedules |  | — |
| MGSG review and approval of design |  | SHTM 02-01 |

Stage 5 – Manufacturing and Construction

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Contractor method statements, detailed phasing, isolation & Permit-to-Work procedures |  | SHTM 02-01 Part B |
| Temporary medical gas supply arrangements (if required) – design, installation & validation |  | SHTM 02-01 Part A |
| Material & equipment certificates (pipework, fittings, terminal units, pendants, plant) |  | SHTM 02-01 Part A |
| Installation of new pipeline systems, valves, AVSUs and terminal units |  | SHTM 02-01 Part A |
| Installation of ceiling pendants / medical supply units (including structural fixings, gas hoses, electrical & data) |  | SHTM 02-01, BS EN ISO 11197 |
| Brazing / jointing records (oxygen-free nitrogen purged, fluxless) |  | SHTM 02-01 Part A |
| Pressure testing, leakage testing and purity / identity testing records |  | SHTM 02-01 Part A |
| Alarm system installation and testing |  | SHTM 02-01 Part A |
| Electrical installation & test certificates associated with pendants (BS 7671) |  | SHTM 06-01 |
| Progress records, quality inspections, change control log & Permit-to-Work records |  | SHTM 02-01 Part B |
| Decommissioning & strip-out records of redundant MGPS / pendants |  | SHTM 02-01 |

Stage 6 – Handover

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Full validation and verification records (carcass, system, performance) as required by SHTM 02-01 Part A |  | SHTM 02-01 Part A |
| Identity, quality, flow and pressure test certificates for all gases and vacuum |  | SHTM 02-01 Part A |
| Pendant performance tests (movement, braking, hose integrity, terminal unit function) |  | SHTM 02-01, manufacturer requirements |
| As-fitted drawings & schematics (including terminal unit schedules and pendant locations) |  | SHTM 02-01 Part A |
| Comprehensive O&M manuals (including pendant maintenance and hose life policy) |  | SHTM 02-01 Part B |
| Updated Health & Safety File |  | CDM |
| Training & demonstration records for Authorised Persons, Competent Persons and clinical users |  | SHTM 02-01 Part B |
| Residual risk register |  | CDM |
| Practical Completion / handover certificate |  | — |
| MGSG acceptance and formal handover of the MGPS |  | SHTM 02-01 |
| Temporary supply decommissioning records (if applicable) |  | SHTM 02-01 |

Stage 7 – Use

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Soft landings / post-occupancy review (system performance, pendant usability, alarm response) |  | SHTM 00 |
| Updated operational procedures, Permit-to-Work arrangements and Written Scheme |  | SHTM 02-01 Part B |
| Ongoing planned preventive maintenance regime (including pendant hose replacement schedule) |  | SHTM 02-01 Part B |
| Defects liability records & final account |  | — |
| Lessons learned report |  | SHTM 00 |

Cross-Stage / Continuous Deliverables

- Live Health & Safety File

- Project risk register (updated at each stage)

- Change control log

- Full Permit-to-Work records

- Medical Gas Safety Group (MGSG) engagement and formal approvals at key gateways

- Evidence of compliance with manufacturer instructions for pendants, terminal units and plant

- Authorised Person (MGPS) oversight throughout design, installation, validation and handover