Detailed HAI-SCRIBE vs RIBA Matrix All 17 Hard FM Systems

1. Standard Alignment between RIBA and HAI-SCRIBE Stages

| RIBA Stage | Typical HAI-SCRIBE Stage(s) | Description of HAI-SCRIBE Focus |
| --- | --- | --- |
| 0 – Strategic Definition | Stage 1 | Initial brief, clinical need, high-level infection risk |
| 1 – Preparation and Briefing | Stage 1 / early Stage 2 | Site/context, project brief, early risk identification |
| 2 – Concept Design | Stage 2 | Design intent, infection risk identification & mitigation strategy |
| 3 – Spatial Coordination | Stage 2 | Coordination of infection-critical design elements |
| 4 – Technical Design | Stage 2 (completion) | Detailed design review, sign-off of infection control measures |
| 5 – Manufacturing & Construction | Stage 3 | Construction risk management, dust, water, pressure, isolation |
| 6 – Handover | Stage 4 | Pre-handover checks, validation, clean, readiness for occupation |
| 7 – Use | Stage 4 (ongoing) | Post-handover feedback, maintenance, operational controls |

2. Detailed Intensity Matrix

HAI-SCRIBE Involvement Level by System and RIBA Stage

Legend

- H = High (formal HAI-SCRIBE process + active IPC involvement expected)

- M = Medium (HAI-SCRIBE applied / IPC input required)

- L = Low (risk-based / limited application)

- – = Generally not significant

| No. | System | RIBA 0 | RIBA 1 | RIBA 2 | RIBA 3 | RIBA 4 | RIBA 5 | RIBA 6 | RIBA 7 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Valve / Boiler Replacement (LTHW) | L | L-M | M | M | M | M-H | M | M |
| 2 | Heating Systems | L | L-M | M | M | M | M-H | M | M |
| 3 | Ventilation Systems | M | M | H | H | H | H | H | H |
| 4 | Medical Gas Systems (incl. Pendants) | M | M | H | H | H | H | H | H |
| 5 | Fire Detection & Alarm Systems | L | L | L-M | L-M | M | M | M | L-M |
| 6 | Lifts | L | L | M | M | M | M-H | M | L-M |
| 7 | Nurse Call & Staff Paging | L | L | L-M | L-M | M | M | M | L-M |
| 8 | Building Management System (BMS) | L | L | M | M | M | M | M | L-M |
| 9 | Electrical Services | L | L | M | M | M | M-H | M | L-M |
| 10 | Domestic Hot & Cold Water | M | M | H | H | H | H | H | H |
| 11 | Chilled Water / Cooling Systems | M | M | H | H | H | H | H | H |
| 12 | Steam Systems | L | L-M | M | M | M | M-H | M | M |
| 13 | Fire Suppression Systems | L | L | M | M | M | M-H | M | L-M |
| 14 | Security Systems | L | L | L-M | L-M | M | M | M | L |
| 15 | Pneumatic Tube Systems | L | L-M | M | M | M | M-H | M | L-M |
| 16 | Above-ground Drainage / Public Health | M | M | H | H | H | H | H | H |
| 17 | Compressed Air (Non-Medical) | L | L | L-M | L-M | M | M | M | L-M |

3. Summary of Highest Priority Systems for HAI-SCRIBE

The following systems require High HAI-SCRIBE involvement across most of the project lifecycle (particularly Stages 2–4 of HAI-SCRIBE / RIBA 2–6):

- Ventilation Systems

- Medical Gas Pipeline Systems

- Domestic Hot & Cold Water Systems

- Chilled Water / Cooling Systems

- Above-ground Drainage / Public Health Systems

These should be prioritised for early and continuous Infection Prevention & Control (IPC) engagement.

Coloured Heat Map – HAI-SCRIBE vs RIBA 17 Hard FM Systems

Colour Legend 🔴 High 🟠 Medium 🟢 Low ⚪ Not significant

| No. | System | R0 | R1 | R2 | R3 | R4 | R5 | R6 | R7 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Valve / Boiler (LTHW) | 🟢 | 🟠 | 🟠 | 🟠 | 🟠 | 🔴 | 🟠 | 🟠 |
| 2 | Heating Systems | 🟢 | 🟠 | 🟠 | 🟠 | 🟠 | 🔴 | 🟠 | 🟠 |
| 3 | Ventilation Systems | 🟠 | 🟠 | 🔴 | 🔴 | 🔴 | 🔴 | 🔴 | 🔴 |
| 4 | Medical Gas Systems | 🟠 | 🟠 | 🔴 | 🔴 | 🔴 | 🔴 | 🔴 | 🔴 |
| 5 | Fire Detection & Alarm | 🟢 | 🟢 | 🟢 | 🟢 | 🟠 | 🟠 | 🟠 | 🟢 |
| 6 | Lifts | 🟢 | 🟢 | 🟠 | 🟠 | 🟠 | 🔴 | 🟠 | 🟢 |
| 7 | Nurse Call & Paging | 🟢 | 🟢 | 🟢 | 🟢 | 🟠 | 🟠 | 🟠 | 🟢 |
| 8 | Building Management System | 🟢 | 🟢 | 🟠 | 🟠 | 🟠 | 🟠 | 🟠 | 🟢 |
| 9 | Electrical Services | 🟢 | 🟢 | 🟠 | 🟠 | 🟠 | 🔴 | 🟠 | 🟢 |
| 10 | Domestic Hot & Cold Water | 🟠 | 🟠 | 🔴 | 🔴 | 🔴 | 🔴 | 🔴 | 🔴 |
| 11 | Chilled Water / Cooling | 🟠 | 🟠 | 🔴 | 🔴 | 🔴 | 🔴 | 🔴 | 🔴 |
| 12 | Steam Systems | 🟢 | 🟠 | 🟠 | 🟠 | 🟠 | 🔴 | 🟠 | 🟠 |
| 13 | Fire Suppression Systems | 🟢 | 🟢 | 🟠 | 🟠 | 🟠 | 🔴 | 🟠 | 🟢 |
| 14 | Security Systems | 🟢 | 🟢 | 🟢 | 🟢 | 🟠 | 🟠 | 🟠 | 🟢 |
| 15 | Pneumatic Tube Systems | 🟢 | 🟠 | 🟠 | 🟠 | 🟠 | 🔴 | 🟠 | 🟢 |
| 16 | Above-ground Drainage | 🟠 | 🟠 | 🔴 | 🔴 | 🔴 | 🔴 | 🔴 | 🔴 |
| 17 | Compressed Air (Non-Medical) | 🟢 | 🟢 | 🟢 | 🟢 | 🟠 | 🟠 | 🟠 | 🟢 |

Visual Summary (Heat Intensity)

| Heat Level | Systems |
| --- | --- |
| 🔴 Hottest (Strong red across most stages) | 3. Ventilation 4. Medical Gases 10. Domestic Hot & Cold Water 11. Chilled Water / Cooling 16. Above-ground Drainage |
| 🟠 Medium | Heating/Boilers, Lifts, Electrical, Steam, Fire Suppression, Pneumatic Tube |
| 🟢 Cooler | Fire Alarm, Nurse Call, BMS, Security, Compressed Air |

This version gives a clear graphical coloured heat map using emoji.