1. Water Systems (SHTM 04-01 Part B)

Water systems include cold/hot water storage, distribution, calorifiers, and outlets. The focus is on temperature control to prevent Legionella, with regular monitoring and cleaning.

| Component | Task | Frequency | Notes |
| --- | --- | --- | --- |
| Cold Water Storage Cisterns | Visual inspection for contamination, corrosion, insulation; clean if required; check valves and pipes. | Annually | Disinfect after cleaning or if contaminated. Drain if unused > few days. |
| Cold Water Distribution | Temperature monitoring at sentinel outlets (below 20°C after 2 min draw-off); visual checks for leaks/corrosion. | Monthly (sentinel); Annually (representative 20% rotation) | Semi-annual at inlet; flush sporadically used outlets twice weekly. |
| Hot Water Storage/Calorifiers | Drain to remove sludge; dismantle and clean; temperature monitoring (flow ≥60°C, return ≥50°C). | Quarterly (drain); Annually (full clean) | Continuous BEMS monitoring; disinfect annually or if temperature <45°C. |
| Hot Water Distribution | Temperature monitoring at sentinel outlets (≥50°C after 1 min); check trace heating. | Monthly (sentinel); Annually (representative) | Flush all outlets regularly; clean and disinfect as needed. |
| Showers/Showerheads | Dismantle, clean, de-scale hoses and heads. | Quarterly | Flush twice weekly if sporadic use; remove unused showers. |
| Point-of-Use Filters | Replace filters; sample water quality. | Monthly | Disinfect outlet if filters removed. |
| General | Legionella testing (if biocide used); risk assessment review. | Monthly (if treated); Every 2 years (risk assessment) | Align with HSE ACOP L8; annual water safety plan review. |

2. Lifts (SHTM 08-02)

Lifts include passenger, goods, and bed lifts. Maintenance ensures safety and reliability, complying with LOLER and PUWER.

| Component | Task | Frequency | Notes |
| --- | --- | --- | --- |
| Overall Lift System | Routine preventive maintenance visits: inspect, adjust, clean pits/car tops/machine rooms; check guide rails, buffers, safety gears. | Monthly (12 visits/year) | Conducted by specialist contractor under comprehensive contract. |
| Safety and Controls | Thorough examination and inspection by competent person. | Every 6 months (or per risk assessment) | Includes overspeed governors, brakes, interlocks; per LOLER. |
| Emergency Systems | Test alarms, emergency lighting, rescue equipment (e.g., hand-winding, lowering valves). | Monthly (alarms); Integrated into routine visits | Verify per BS EN 81-28; annual audit includes performance tests. |
| Cleaning | Clean pits, car tops, machine rooms of dirt/detritus; clean car interiors, doors, tracks. | Monthly | Part of routine visits; staff can check daily for cleanliness. |
| Lubrication | Lubricate guide rails, ropes, moving parts. | As part of monthly routine | Follow manufacturer instructions; check during audits. |
| General | Annual maintenance audit: physical checks, ride quality, statutory compliance. | Annually | Staff perform regular checks (e.g., ride test, noise, leveling). |

3. Ventilation Systems (SHTM 03-01 Part B)

Ventilation includes HVAC, air handling units (AHUs), ducts, and filters. PPM focuses on performance verification, hygiene, and energy efficiency. (Note: Specific frequencies are based on risk; high-risk areas like theatres may require more frequent tasks.)

| Component | Task | Frequency | Notes |
| --- | --- | --- | --- |
| Air Handling Units (AHUs) | Inspect for condition, clean coils/heat exchangers; check belts, motors, dampers. | Quarterly to Annually | Clean if contaminated; verify airflow and pressure differentials. |
| Filters | Inspect and replace pre-filters, bag filters, HEPA filters. | Monthly inspection; Replacement: Pre-filters (3-6 months), Bag (6-12 months), HEPA (annually or when dirty) | In high-risk areas (e.g., theatres), test HEPA integrity annually. |
| Ducts | Inspect for cleanliness, leaks; clean internal surfaces. | Annually (inspection); Every 2-5 years (cleaning, based on risk) | Use access doors for inspection; more frequent in dirty environments. |
| Fans and Blowers | Inspect bearings, lubrication; check vibration, alignment. | Quarterly | Lubricate as needed; balance annually if vibration issues. |
| General | Performance verification: airflow measurements, pressure tests; microbiological sampling if needed. | Annually | Risk-based; align with CIBSE and BS EN standards; annual system audit. |

4. Medical Gas Pipeline Systems (SHTM 02-01 Part B)

Includes oxygen, medical air, vacuum, and manifolds. PPM ensures gas quality and system integrity.

| Component | Task | Frequency | Notes |
| --- | --- | --- | --- |
| Manifolds | Inspect cylinders, valves, regulators; test automatic changeover. | Quarterly | Check pressure, leaks; replace cylinders as needed. |
| Compressors (Medical Air) | Inspect filters, dryers, oil levels; clean/replace elements; test gas quality (e.g., CO2 <500 ppm). | Monthly (filters); Quarterly (full service) | Annual gas purity test; continuous monitoring if available. |
| Vacuum Plants | Inspect pumps, receivers, filters; check oil, belts; test suction levels. | Quarterly | Drain receivers weekly; annual performance test. |
| Terminal Units | Inspect for damage, leaks; test self-sealing valves. | Annually | More frequent in high-use areas; clean externally monthly. |
| General | System inspection for leaks, labeling; gas quality testing; permit-to-work for maintenance. | Annually (full system) | Risk assessment every 2 years; align with BS EN ISO standards. |

5. Electrical Services (SHTM 06-01 Part B)

Includes supply, distribution, generators, and UPS. PPM ensures resilience and safety.

| Component | Task | Frequency | Notes |
| --- | --- | --- | --- |
| Generators | Load test, fuel check, battery inspection; full service. | Monthly (run test); Annually (load bank test) | Simulate mains failure quarterly; check oil/fuel annually. |
| UPS Systems | Battery inspection, discharge test; clean filters. | Monthly (visual); Annually (discharge) | Replace batteries every 3-5 years; monitor via BEMS. |
| Switchgear | Inspect for corrosion, connections; thermal imaging. | Annually | Clean and test breakers; 5-year fixed wiring inspection per BS 7671. |
| Wiring and Distribution | Visual inspection for damage; earth continuity test. | Annually (visual); Every 5 years (full test) | Risk-based; more frequent in critical areas. |
| General | System audit, emergency lighting test. | Monthly (lighting function); Annually (full audit) | Comply with BS 7671; electricity safety group oversight. |

6. Fire Safety Systems (SHTM 81, 82, 83)

Fire systems include alarms, extinguishers, doors, and sprinklers. PPM is covered in SHTM 83 for general precautions and SHTM 82 for alarms.

| Component | Task | Frequency | Notes |
| --- | --- | --- | --- |
| Fire Alarms | Test call points, detectors, sounders. | Weekly (one zone/call point); Quarterly (full system) | Annual service by competent person; per BS 5839. |
| Extinguishers | Visual inspection for damage, pressure. | Monthly | Annual service; replace every 5-10 years. |
| Fire Doors | Inspect closers, seals, operation. | Quarterly | Ensure self-closing; annual full check. |
| Sprinklers (if installed) | Inspect heads, valves; flow test. | Weekly (valves); Annually (full test) | Per BS EN 12845; drain and flush as needed. |
| General | Fire risk assessment review; emergency lighting test. | Annually (assessment); Monthly (lighting) | Align with Fire (Scotland) Act; staff training annually. |

For additional assets like building fabric (roofs, doors), PPM is per SHTM 00 (general engineering) with annual inspections. Sanitary assemblies (SHTM 64) require quarterly cleaning. Always consult the full SHTM documents and conduct site-specific risk assessments for compliance. If changes occur (e.g., refurbishment), review and update schedules.