Heating System Upgrade (Boiler + Valve Replacement)
What the Project Manager should look for in each deliverable

Gate 0 — Strategic Definition

| Deliverable | What the PM should look for |
| --- | --- |
| Business case | Clear problem statement, consequences of doing nothing, and why action is needed now. |
| Strategic brief & outcomes | Measurable outcomes (continuous heating, resilience, boiler replacement). |
| High-level clinical / operational impact assessment | Evidence of clinical consideration if heating is lost. |

PM focus: Confirm the problem is real and worth solving.

Gate 1 — Preparation & Briefing

| Deliverable | What the PM should look for |
| --- | --- |
| Updated Project Brief | Scope clearly covers both valves and full boiler replacement. |
| Existing plant condition surveys | Actual survey reports with condition evidence. |
| Initial water quality baseline sampling | Baseline results before any work starts. |
| Early awareness engagement with Water Safety Group | Record that WSG has been notified (not formal approval yet). |
| Expanded Risk Register | Live register covering continuity, temporary plant, water, combustion, CDM. |
| Project Execution Plan & procurement strategy | Clear buying route and roles. |

PM focus: Do we properly understand the starting position?

Gate 2 — Concept Design

| Deliverable | What the PM should look for |
| --- | --- |
| Concept options for boiler replacement | Realistic options considered and a preferred direction emerging. |
| Temporary boiler strategy | Size, location and how heating will be maintained. |
| Outline mechanical services strategy | High-level description of new plant and key components. |
| Preliminary flue / combustion / fuel strategy | Early consideration of flues, air and fuel supplies. |
| Outline specifications & preliminary cost plan | Early cost range with contingency. |
| Design risk assessment | High-level risks only. |

PM focus: Have we chosen a sensible direction? (No detailed drawings or method statements expected.)

Gate 3 — Spatial Coordination

| Deliverable | What the PM should look for |
| --- | --- |
| Fire compartmentation impact assessment | Fire Officer involvement or formal comment. |
| Coordinated layout | Shows new boilers, temporary boilers, main routes and access. |
| Confirmation of temporary & permanent plant arrangements | Written high-level confirmation only. |
| Spatial coordination with structure & other services | Evidence that major clashes have been checked. |
| Updated cost plan, risk register & high-level phasing | Still principles only — no detailed method statements. |
| HAI-SCRIBE review | Record that infection control impact has been considered. |

PM focus: Will it fit and can we keep the hospital running?

Gate 4 — Technical Design

(Critical Commercial & Governance Gate)

| Deliverable | What the PM should look for |
| --- | --- |
| PRE-CONTRACT HOLD POINT | This is the key control point. |
| Developed design / performance specifications | Enough detail to price accurately — not full construction drawings. |
| Detailed Scope of Works | Clear inclusions and exclusions. |
| Updated cost plan including contingency | Realistic budget the Board can approve. |
| Water treatment / corrosion strategy | Suitable for WSG review. |
| BMS, Electrical, Flue, Structural, Insulation information | Sufficient for pricing and coordination. |
| Pre-Construction Information (PCI) | CDM hazards and design risks captured. |
| Tender documentation | Package actually issued for quotes. |
| Minimum two competitive quotations | Comparable quotes on the same scope. |
| Formal SBAR submitted to Water Safety Group | Written SBAR document. |
| Written WSG approval | Signed or minuted approval. |
| Board / PFI cost approval | Formal written approval. |
| DSEAR risk assessment (fuel supply / combustion) | Confirm a genuine DSEAR risk assessment exists for the boiler fuel supply, not just a generic COSHH line. |

PM focus:
Do not allow contractor appointment or Gate 5 to start until you have:

- Two comparable quotes

- Written WSG approval

- Written Board / PFI cost approval

Gate 5 — Manufacturing & Construction

(Only after Hold Point is cleared)

| Deliverable | What the PM should look for |
| --- | --- |
| Contractor’s detailed Method Statements & full RAMS | Only appear after appointment. Check they match the approved scope. |
| Temporary boiler installation & commissioning certificates | Evidence that temporary boilers are installed, tested and working before permanent boilers are taken offline. |
| Hot tapping / isolation verification records | Proof that isolations were carried out safely and verified. |
| Permanent boiler installation records | Delivery, installation, flue and fuel connection evidence. |
| Material & equipment certificates | Boilers, valves, pumps, filtration, etc. |
| Water sampling results (pre-, interim-, post-works) | Shows water quality was monitored throughout. |
| Flushing, cleaning & chemical treatment records | Required under SHTM 04-01. |
| BMS & electrical installation & test certificates | Point-to-point testing and BS 7671 certificates. |
| Combustion, efficiency & safety interlock testing | Boilers have been safely commissioned. |
| Progress records, quality inspections & change control | Live records of what is happening on site. |
| Decommissioning records of old boilers | Safe isolation and strip-out evidence. |
| Evidence of current PVG Scheme membership for contractor personnel | Confirm named operatives attending site hold current PVG Scheme membership, not just trade qualifications. |

PM focus:
Is the work being done in accordance with the approved scope and temporary strategy?
Are the safety and water quality records being generated as the work proceeds?

Gate 6 — Handover

| Deliverable | What the PM should look for |
| --- | --- |
| Full system testing & commissioning records | Complete set covering boilers, LTHW circuit, pumps and controls. |
| Boiler performance / efficiency / emissions certificates | Proof the new boilers meet the required performance. |
| Balancing / flow verification data | System is hydraulically balanced. |
| As-fitted drawings & schematics | Accurate record of what was actually installed. |
| Comprehensive O&M manuals | Usable manuals for the new plant. |
| Updated Health & Safety File | CDM requirement. |
| Training & demonstration records | Estates / Serco staff have been trained. |
| Residual risk register | Any remaining risks are documented. |
| Practical Completion / handover certificate | Formal handover document. |
| Final water quality & corrosion monitoring baseline | New baseline after works. |
| Temporary boiler decommissioning & removal certificates | Temporary plant has been safely removed. |
| Updated Water Safety Plan / Written Scheme submitted to WSG | Formal close-out with Water Safety Group. |

PM focus:
Can the hospital safely operate and maintain the new system?
Have all statutory and WSG close-out items been completed?

Gate 7 — Use

| Deliverable | What the PM should look for |
| --- | --- |
| Soft landings / post-occupancy review | Feedback on actual performance, any early issues, and user experience. |
| Ongoing monitoring regime | Filtration, corrosion coupons, boiler efficiency monitoring is in place. |
| Defects liability records & final account | Defects are being managed and the account is being closed. |
| Lessons learned report | What went well and what should be done differently next time. |

PM focus:
Is the system performing as expected and have we captured lessons for future projects?

Quick PM Summary

| Gate | One-sentence question for the PM |
| --- | --- |
| 0 | Is this problem real? |
| 1 | Do we understand the starting position? |
| 2 | Have we chosen a sensible direction? |
| 3 | Will it fit and can we keep the hospital running? |
| 4 | Do we have robust prices and the required approvals before appointing a contractor? |
| 5 | Is the work being delivered safely and in line with the approved scope? |
| 6 | Can the hospital safely take over and operate the new system? |
| 7 | Is it performing and have we learned from it? |