Project assumption update: In addition to the original valve replacement works, the three existing 7 MW dual-fuel boilers are now assumed to require full replacement. Temporary boilers remain essential to maintain continuous heating and system resilience throughout the works.

Primary SHTM / guidance references (unchanged core set, with boiler-related emphasis):

- SHTM 00 – Policies and principles

- SHTM 04-01 (Parts A, B, D, E, G) – Water safety (LTHW closed systems, treatment, filtration, corrosion monitoring, flushing, sampling)

- SHTM 06-01 – Electrical services

- Supporting: CDM 2015, HSE ACOP L8 / HSG 274, Pressure Systems Safety Regulations (PSSR), BSRIA water treatment guidance, CIBSE Guides, relevant BS/EN standards for boilers, flues, gas/oil systems, and combustion equipment.

Stages 0–3 are assumed largely complete or in progress; the checklist covers the full lifecycle.

Stage 0 – Strategic Definition

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Business case (valve isolation failure + boiler condition / end-of-life risk) |  | SHTM 00 |
| Strategic brief & outcomes (continuous heating, full resilience, boiler replacement) |  | SHTM 00 |
| High-level clinical / operational impact assessment |  | SHTM 00 |

Stage 1 – Preparation and Briefing

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Updated Project Brief (valve replacement + full boiler replacement) |  | SHTM 00 |
| Existing plant condition surveys (boilers, flues, gas/oil systems, foundations) |  | SHTM 00, SHTM 04-01 |
| Initial water quality baseline sampling |  | SHTM 04-01 Part A |
| Risk register (heating continuity, temporary plant, gas/fuel, combustion, structural) |  | SHTM 00, CDM |
| Project Execution Plan & procurement strategy |  | — |

Stage 2 – Concept Design

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Concept options for boiler replacement strategy (capacity, dual-fuel, efficiency, phasing) |  | SHTM 00 |
| Temporary boiler strategy (sizing, location, connections) to cover permanent boiler changeover |  | SHTM 00, SHTM 04-01 |
| Outline mechanical services strategy (new boilers, headers, valves, pumps, filtration, corrosion monitoring) |  | SHTM 04-01 Part A |
| Preliminary flue / combustion air / gas & oil supply strategy |  | — |
| Outline specifications & preliminary cost plan |  | — |
| Design risk assessment |  | CDM, SHTM 00 |

Stage 3 – Spatial Coordination

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Coordinated layout (new boiler positions, temporary boilers, pipework, flues, access) |  | SHTM 00 |
| Spatial coordination of mechanical, electrical, BMS, structural supports / plinths |  | SHTM 06-01 |
| Updated cost plan, risk register & phasing strategy |  | — |
| Confirmation of temporary boiler siting and permanent boiler plantroom arrangement |  | — |

Stage 4 – Technical Design

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Full technical design drawings & schematics (including phasing, temporary & permanent boiler arrangements) |  | SHTM 04-01 Part A |
| Detailed specifications: |  |  |
| – New dual-fuel boilers (capacity, efficiency, emissions) |  |  |
| – Valves, headers, pipework, pumps |  |  |
| – Side-stream filtration & corrosion monitoring |  |  |
| – Temporary boilers |  | SHTM 04-01, manufacturer data |
| Flue system design, combustion air, gas & oil supply modifications |  | — |
| Water treatment / chemical dosing / corrosion inhibitor strategy |  | SHTM 04-01 Part A + BSRIA |
| BMS control philosophy, sequences & point schedules (new boilers + retained systems) |  | SHTM 06-01 |
| Electrical design (boiler power, controls, temporary plant) |  | SHTM 06-01 |
| Structural / plinth / support design information |  | — |
| Thermal insulation specification |  | — |
| Building Regulations / statutory compliance information (including energy / emissions) |  | — |
| Pre-construction information & input to Construction Phase Plan |  | CDM |
| Designer’s Risk Assessment & residual risks |  | CDM, SHTM 00 |
| Tender documentation / updated SOW / pricing schedules |  | — |

Stage 5 – Manufacturing and Construction

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Contractor method statements, detailed phasing & temporary works designs |  | — |
| Temporary boiler installation, connection, load testing & commissioning certificates |  | SHTM 00 |
| Hot tapping / isolation verification records |  | — |
| New permanent boiler delivery, installation, flue connections, gas/oil connections |  | — |
| Material & equipment certificates (boilers, valves, pumps, filtration, pipework) |  | SHTM 04-01 |
| Water sampling results (pre-, interim- and post-works) |  | SHTM 04-01 Parts A/B/C |
| System flushing, cleaning, chemical treatment & inhibitor dosing records |  | SHTM 04-01 Part D |
| Installation of new headers, valves, pumps, side-stream filtration & corrosion monitoring |  | SHTM 04-01 |
| BMS installation, wiring, point-to-point testing & sequence proving |  | SHTM 06-01 |
| Electrical installation & test certificates (BS 7671) |  | SHTM 06-01 |
| Combustion, efficiency, emissions and safety interlock testing of new boilers |  | — |
| Thermal insulation completion |  | — |
| Progress records, quality inspections & change control log |  | — |
| Decommissioning records for existing boilers (safe isolation, strip-out) |  | — |

Stage 6 – Handover

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Full system testing & commissioning records (new boilers, LTHW circuit, pumps, controls) |  | SHTM 04-01 Part A |
| Boiler performance / efficiency / emissions test certificates |  | — |
| Balancing / flow verification data |  | SHTM 04-01 |
| As-fitted drawings & schematics (boilers, valves, isolation points, filtration, corrosion monitoring) |  | SHTM 04-01 |
| Comprehensive O&M manuals (including new boilers, temporary plant removal records) |  | SHTM 00, SHTM 04-01 Part B |
| Updated Health & Safety File |  | CDM |
| Training & demonstration records for Serco / estates staff (new boilers & isolation procedures) |  | SHTM 00 |
| Residual risk register |  | CDM |
| Practical Completion / handover certificate |  | — |
| Final water quality, inhibitor residual & corrosion monitoring baseline report |  | SHTM 04-01 |
| Temporary boiler decommissioning & site removal certificates |  | — |

Stage 7 – Use

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Soft landings / post-occupancy review (boiler performance, isolation capability, water quality) |  | SHTM 00 |
| Updated Water Safety Plan / Written Scheme (if required by Water Safety Group) |  | SHTM 04-01 Parts B & G |
| Ongoing monitoring regime (side-stream filtration, corrosion coupons, boiler efficiency) |  | SHTM 04-01 Part B |
| Defects liability records & final account |  | — |
| Lessons learned report |  | SHTM 00 |

Cross-Stage / Continuous Deliverables

- Live Health & Safety File

- Project risk register (updated each stage)

- Change control log

- Water Safety Group (WSG) engagement and approvals for system modifications

- Evidence of compliance with manufacturer instructions for new boilers, temporary boilers, valves and filtration equipment

- Pressure Systems Safety Regulations (PSSR) written scheme of examination updates (if applicable to new boilers)