Deliverables Checklist Replacement / Upgrade of Chilled Water / Cooling Systems in a Hospital Aligned to RIBA Plan of Work 2020 & relevant SHTMs

This checklist follows the exact same format as the Electrical Services, Domestic Hot & Cold Water, Medical Gas, Lifts and BMS checklists. It is intended for projects involving the replacement, major upgrade or significant modification of Chilled Water and Cooling Systems in hospital premises (chillers, chilled water distribution, pumps, pressurisation, fan coil units, AHU cooling coils, free cooling, and associated controls).

Primary SHTM / Guidance References

| System Element | Key Guidance |
| --- | --- |
| Chilled Water / Cooling Systems | SHTM 03-01 – Specialised ventilation for healthcare premises (strongly linked for cooling of critical areas) SHTM 00 – Policies and principles |
| Supporting | SHTM 06 series (Electrical power to chillers/pumps) SHTM 04-01 (if water treatment interfaces) BMS integration |
| Core Standards | CIBSE Guides (especially Guide B and Guide H) BSRIA guidance (BG documents on commissioning and water treatment) BS EN standards for chillers and pipework F-Gas Regulations (if applicable) CDM 2015 |

Key Principles

- Continuity of cooling to critical clinical areas (theatres, critical care, laboratories, pharmacy, data rooms, etc.) must be maintained.

- Resilience (N+1 or greater) is normally required for critical cooling loads.

- Water treatment, corrosion control and microbiological management of the closed chilled water system are essential.

- Energy efficiency, free cooling and part-load performance should be prioritised.

- Full integration with the BMS for monitoring, control and alarming is required.

Stage 0 – Strategic Definition

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Business case / need identification (system age, capacity, resilience, energy performance, critical cooling risks) |  | SHTM 00, SHTM 03-01 |
| Strategic brief & project outcomes (clinical resilience, continuity of cooling, energy efficiency, future capacity) |  | SHTM 00 |
| High-level clinical / operational impact assessment |  | SHTM 00, SHTM 03-01 |

Stage 1 – Preparation and Briefing

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Project Brief (scope of chilled water / cooling works, resilience requirements, critical areas) |  | SHTM 00, SHTM 03-01 |
| Existing system condition surveys (chillers, CHW pipework, pumps, pressurisation, coils, water quality) |  | — |
| Cooling load assessment and residual capacity analysis |  | CIBSE |
| Initial risk register (loss of cooling, critical areas, water treatment, refrigerants) |  | SHTM 00, CDM |
| Project Execution Plan & procurement strategy |  | — |
| Engagement with clinical, estates and energy stakeholders |  | SHTM 00 |

Stage 2 – Concept Design

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Concept design options (chiller type, air-cooled vs water-cooled, free cooling, resilience philosophy, distribution strategy) |  | SHTM 03-01, CIBSE |
| Outline cooling strategy (temperatures, flow rates, primary/secondary, buffer vessels) |  | CIBSE |
| Preliminary schematics and load schedules |  | — |
| Outline specifications & preliminary cost plan |  | — |
| Design risk assessment |  | CDM, SHTM 00 |

Stage 3 – Spatial Coordination

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Coordinated design (chiller locations, pipe routes, pump rooms, access, external plant) |  | SHTM 00 |
| Spatial coordination with structure, electrical, ventilation, fire compartments and other services |  | SHTM 00 |
| Updated cost plan, risk register & high-level phasing / temporary cooling strategy |  | — |
| Confirmation of resilience and free-cooling provisions |  | — |

Stage 4 – Technical Design

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Full technical design drawings, schematics and pipework layouts |  | CIBSE, manufacturer data |
| Detailed specifications (chillers, pumps, pipework, valves, insulation, pressurisation, water treatment, controls) |  | CIBSE, BSRIA |
| Water treatment / chemical dosing / corrosion and microbiological control strategy |  | BSRIA, SHTM 04-01 principles |
| Control strategy, sequences and BMS point schedules |  | SHTM 03-01 linked, CIBSE Guide H |
| Electrical design associated with chillers, pumps and controls |  | SHTM 06 series |
| Refrigerant management and F-Gas compliance (if applicable) |  | F-Gas Regulations |
| Building Regulations / statutory compliance information |  | — |
| Pre-construction information & input to Construction Phase Plan |  | CDM |
| Designer’s Risk Assessment & residual risks |  | CDM, SHTM 00 |
| Tender documentation / Scope of Works / pricing schedules |  | — |
| Stakeholder review and approval of design |  | SHTM 00 |

Stage 5 – Manufacturing and Construction

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Contractor method statements, detailed phasing & temporary cooling arrangements |  | Critical for clinical areas |
| Material & equipment certificates (chillers, pumps, pipework, valves, insulation) |  | Manufacturer |
| Installation of chillers, pipework, pumps, pressurisation units, insulation and controls |  | — |
| Pressure testing, flushing, cleaning and chemical treatment records |  | BSRIA |
| Water sampling and quality records |  | — |
| Progress records, quality inspections, change control log |  | — |
| Temporary cooling / hybrid working arrangements (if phased) |  | Essential |
| Decommissioning & strip-out records of redundant cooling equipment |  | — |

Stage 6 – Handover

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Full commissioning & validation records (flow rates, temperatures, pressures, chiller performance, control sequences) |  | CIBSE, BSRIA |
| Performance testing at part-load and design conditions |  | — |
| Water treatment verification and baseline quality report |  | — |
| As-fitted drawings, schematics, valve schedules and control logic |  | — |
| Comprehensive O&M manuals |  | SHTM 00 |
| Updated Health & Safety File |  | CDM |
| Training & demonstration records for estates and energy staff |  | SHTM 00 |
| Residual risk register |  | CDM |
| Practical Completion / handover certificate |  | — |
| Formal client / stakeholder acceptance |  | — |

Stage 7 – Use

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Soft landings / post-occupancy review (cooling performance, energy, resilience, user feedback) |  | SHTM 00 |
| Updated maintenance regime, water treatment programme and monitoring procedures |  | — |
| Ongoing performance and energy monitoring |  | — |
| Defects liability records & final account |  | — |
| Lessons learned report |  | SHTM 00 |

Cross-Stage / Continuous Deliverables

- Live Health & Safety File

- Project risk register (updated at each stage)

- Change control log

- Stakeholder engagement (estates, clinical, energy, infection control) at key gateways

- Maintenance of continuous cooling to critical clinical areas throughout the works

- Evidence of compliance with CIBSE, BSRIA, F-Gas (where applicable) and manufacturer requirements

- Full water treatment and system cleanliness records