Deliverables Checklist Replacement / Upgrade of Fire Detection and Alarm Systems in a Hospital Aligned to RIBA Plan of Work 2020 & relevant SHTMs

This checklist follows the same format as the previous medical gas, heating/ventilation and valve/boiler checklists. It is intended for projects involving the replacement, major upgrade or significant modification of fire detection and alarm systems in hospital premises.

Primary SHTM / guidance references

| System Element | Key Guidance |
| --- | --- |
| Fire Detection & Alarm Systems | SHTM 82 – NHSScotland Firecode: Fire detection and alarm systems (current version – V5 Sept 2025) |
| Supporting Firecode | SHTM 81 (Fire safety in the design of healthcare premises) SHTM 83 (General fire precautions) SHTM 86 (Fire risk assessment) SHTM 00 (Policies and principles) |
| Core Standards | BS 5839-1 (Fire detection and fire alarm systems for buildings) Category L1 addressable system required throughout hospitals |
| Other | CDM 2015 Reduction of Unwanted Fire Alarm Signals (UFAS) guidance within SHTM 82 |

Key principles

- Hospitals require a Category L1 addressable automatic fire detection and alarm system throughout.

- Fire alarm zones must align with fire compartment / sub-compartment boundaries.

- Strong emphasis on minimising Unwanted Fire Alarm Signals (UFAS).

- System must interface correctly with other fire safety measures (e.g. door release, smoke control, lifts, plant shutdown where required).

- Continuity of protection must be maintained during the works (phased working or temporary cover).

Stage 0 – Strategic Definition

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Business case / need identification (system age, reliability, UFAS performance, compliance) |  | SHTM 00, SHTM 82 |
| Strategic brief & project outcomes (life safety, continuity of protection, UFAS reduction) |  | SHTM 00 |
| High-level clinical / operational impact assessment |  | SHTM 00, SHTM 86 |

Stage 1 – Preparation and Briefing

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Project Brief (scope of system replacement / upgrade, continuity requirements) |  | SHTM 00, SHTM 82 |
| Existing system condition survey (panels, detectors, call points, cabling, cause & effect) |  | SHTM 82, BS 5839-1 |
| Baseline UFAS data and false alarm analysis |  | SHTM 82 |
| Initial risk register (protection during works, zone integrity, interface risks) |  | SHTM 00, CDM, SHTM 86 |
| Project Execution Plan & procurement strategy |  | — |
| Engagement with Fire Safety Advisor / Fire Safety Group |  | SHTM 82, SHTM 86 |

Stage 2 – Concept Design

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Concept design options (full replacement vs phased upgrade, technology choice) |  | SHTM 82 |
| Outline detection & alarm strategy (Category L1 addressable, zoning, interfaces) |  | SHTM 82, BS 5839-1 |
| Preliminary detector type selection (multi-sensor preference to reduce UFAS) |  | SHTM 82 |
| Outline specifications & preliminary cost plan |  | — |
| Design risk assessment |  | CDM, SHTM 00, SHTM 82 |

Stage 3 – Spatial Coordination

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Coordinated design (device locations, cable routes, panel positions, zone plans) |  | SHTM 82 |
| Spatial coordination with structure, ceilings, other services and fire compartments |  | SHTM 81 |
| Updated cost plan, risk register & high-level phasing / temporary cover strategy |  | — |
| Confirmation of zone boundaries aligned to compartments |  | SHTM 82 |

Stage 4 – Technical Design

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Full technical design drawings, schematics and zone plans |  | SHTM 82, BS 5839-1 |
| Detailed specifications (CIE, detectors, manual call points, sounders, visual devices, cabling, power supplies) |  | SHTM 82, BS 5839-1 |
| Cause & effect matrix / interface schedule (doors, plant, lifts, smoke control, etc.) |  | SHTM 82 |
| Battery autonomy and power supply design |  | BS 5839-1 |
| UFAS reduction strategy (detector selection, multi-criteria, verification technology) |  | SHTM 82 |
| Building Regulations / statutory compliance information |  | — |
| Pre-construction information & input to Construction Phase Plan |  | CDM |
| Designer’s Risk Assessment & residual risks |  | CDM, SHTM 82 |
| Tender documentation / Scope of Works / pricing schedules |  | — |
| Fire Safety Advisor / stakeholder review and approval of design |  | SHTM 82 |

Stage 5 – Manufacturing and Construction

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Contractor method statements, detailed phasing & temporary protection arrangements |  | SHTM 82 |
| Material & equipment certificates (panels, detectors, devices, cable) |  | BS 5839-1 |
| Installation of new control and indicating equipment (CIE), detectors, call points, sounders and visual alarms |  | SHTM 82, BS 5839-1 |
| Cable installation, containment and labelling records |  | BS 5839-1 |
| Interface installation and testing records |  | SHTM 82 |
| Progress records, quality inspections, change control log |  | — |
| Temporary system cover / hybrid working arrangements (if phased) |  | SHTM 82 |
| Decommissioning & strip-out records of redundant equipment |  | — |

Stage 6 – Handover

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Full commissioning and verification records in accordance with BS 5839-1 and SHTM 82 |  | SHTM 82, BS 5839-1 |
| Cause & effect testing and sign-off |  | SHTM 82 |
| As-fitted drawings, zone plans and device schedules |  | SHTM 82 |
| Comprehensive O&M manuals and log book |  | SHTM 82, BS 5839-1 |
| Updated Health & Safety File |  | CDM |
| Training & demonstration records for estates staff and fire response teams |  | SHTM 82, SHTM 83 |
| Residual risk register |  | CDM |
| Practical Completion / handover certificate |  | — |
| Formal acceptance by Fire Safety Advisor / Responsible Person |  | SHTM 82 |
| Updated fire risk assessment (SHTM 86) reflecting the new system |  | SHTM 86 |

Stage 7 – Use

| Deliverable | Status / Evidence | Relevant SHTM / Notes |
| --- | --- | --- |
| Soft landings / post-occupancy review (system performance, UFAS rates, user feedback) |  | SHTM 00 |
| Updated fire safety management procedures and training materials |  | SHTM 83 |
| Ongoing planned preventive maintenance and testing regime (BS 5839-1) |  | SHTM 82 |
| UFAS monitoring and reduction action plan |  | SHTM 82 |
| Defects liability records & final account |  | — |
| Lessons learned report |  | SHTM 00 |

Cross-Stage / Continuous Deliverables

- Live Health & Safety File

- Project risk register (updated at each stage)

- Change control log

- Engagement with Fire Safety Advisor / Fire Safety Group at key gateways

- Evidence of compliance with manufacturer instructions and BS 5839-1 certification

- Maintenance of adequate fire detection and alarm cover throughout the works